## DA Results (hidden)
DA results
|  |  | TTC Adjustment |  |  | TTC Validated |  |  | ANTC |  |  | LimitedBy | [8 empty] | AT | AT | AT | AT | AT | AT | CH | CH | CH | CH | CH | CH | FR | FR | FR | FR | FR | FR | SI | SI | SI | SI | SI | SI | IT | IT |  |  | IT | IT | IT | IT | IT
Business day | Month | Timestamp | TTC_Full_Import | TTCImport | TTCExport | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | 70% red | TTCRed_Import | TTCRed_Transit_Import | TTCRed_Transit_Export | TTCRed_Transit | TTC and 70% red | FLAG | Bilateral | MNII | Reason | Bilateral - Export | MNIE | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - Export | MIEC | Reason | Bilateral- Import OutArea FR | Bilateral- Import OutArea CH | Bilateral- Import OutArea AT | Bilateral- Import OutArea SI | MNII | Reason | Bilateral - Export | MIEC | Reason
20250401 | April | 30 | 7815 |  |  | 7815 |  |  | -4387 | -4387 | -4386 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 170
20250401 | April | 130 | 7815 |  |  | 7815 |  |  | -4387 | -4387 | -4386 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 366; AT: 170
20250401 | April | 230 | 7815 |  |  | 7815 |  |  | -4387 | -4387 | -4386 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 366; AT: 170
20250401 | April | 330 | 7282 |  |  | 7282 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 366; AT: 170
20250401 | April | 430 | 7282 |  |  | 7282 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 364; AT: 170
20250401 | April | 530 | 7282 |  |  | 7282 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 205; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 630 | 7082 |  |  | 7081 |  |  | -3251 | -3251 | -3250 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 208; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 730 |  | 8191 | 1067 |  | 7868 | 1032 | 3379 | 185 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3194 | NA | 323 | 35 | 358 | -185 | 1 | AT: 349; AT: 155
20250401 | April | 830 |  | 8191 | 1067 |  | 7868 | 1032 | 3379 | 185 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3194 | NA | 323 | 35 | 358 | -185 | 1 | AT: 349; AT: 155
20250401 | April | 930 | 7225 |  |  | 7215 |  |  | 3929 | 235 | 3704 | Minimum Margin | Validation phase | 3694 | 10 | NA | NA | NA | 7173 | 1 | AT: 349; AT: 155
20250401 | April | 1030 | 7225 |  |  | 7215 |  |  | 3929 | 235 | 3704 | Minimum Margin | Validation phase | 3694 | 10 | NA | NA | NA | 7173 | 1 | AT: 424; AT: 155
20250401 | April | 1130 | 7225 |  |  | 7215 |  |  | 3929 | 235 | 3704 | Minimum Margin | Validation phase | 3694 | 10 | NA | NA | NA | 7173 | 1 | AT: 424; AT: 155
20250401 | April | 1230 | 8674 |  |  | 8633 |  |  | -1422 | -1422 | -1381 | Critical Branch | Validation phase | 0 | 41 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155
20250401 | April | 1330 | 8674 |  |  | 8633 |  |  | -1422 | -1422 | -1381 | Critical Branch | Validation phase | 0 | 41 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155
20250401 | April | 1430 | 8674 |  |  | 8633 |  |  | -1422 | -1422 | -1381 | Critical Branch | Validation phase | 0 | 41 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155
20250401 | April | 1530 | 8666 |  |  | 8666 |  |  | -1143 | -1143 | -1143 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 424; AT: 155
20250401 | April | 1630 | 8666 |  |  | 8666 |  |  | -1143 | -1143 | -1143 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 147; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 1730 | 8666 |  |  | 8666 |  |  | -1143 | -1143 | -1143 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 147; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 1830 |  | 9059 | 899 |  | 8640 | 899 | -6540 | -6540 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 419 | 0 | 419 | 6540 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 147; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 1930 |  | 9059 | 899 |  | 8640 | 899 | -6540 | -6540 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 419 | 0 | 419 | 6540 | 1 | AT: 399; AT: 155
20250401 | April | 2030 |  | 9059 | 899 |  | 8640 | 899 | -6540 | -6540 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 419 | 0 | 419 | 6540 | 1 | AT: 399; AT: 155
20250401 | April | 2130 | 8367 |  |  | 8366 |  |  | -4888 | -4888 | -4888 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 381; AT: 170
20250401 | April | 2230 | 8367 |  |  | 8366 |  |  | -4888 | -4888 | -4888 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 385; AT: 170
20250401 | April | 2330 | 7557 |  |  | 7557 |  |  | -4078 | -4078 | -4077 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 170
20250402 | April | 30 | 7637 |  |  | 7636 |  |  | -3279 | -3279 | -3278 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 385; AT: 170
20250402 | April | 130 | 7637 |  |  | 7636 |  |  | -3279 | -3279 | -3278 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 355; AT: 170
20250402 | April | 230 | 7637 |  |  | 7636 |  |  | -3279 | -3279 | -3278 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 355; AT: 170
20250402 | April | 330 | 7078 |  |  | 7078 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 355; AT: 170
20250402 | April | 430 | 7078 |  |  | 7078 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 353; AT: 170
20250402 | April | 530 | 7078 |  |  | 7078 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 409; AT: 155
20250402 | April | 630 | 6878 |  |  | 6878 |  |  | -1908 | -1908 | -1907 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 417; AT: 155
20250402 | April | 730 | 8541 |  |  | 8378 |  |  | -5293 | -5293 | -5133 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 163 | NA | NA | NA | 0 | 1 | AT: 350; AT: 155
20250402 | April | 830 | 8541 |  |  | 8540 |  |  | -5293 | -5293 | -5293 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 350; AT: 155
20250402 | April | 930 | 7250 |  |  | 7245 |  |  | 972 | 260 | 716 | Minimum Margin | Validation phase | 712 | 5 | NA | NA | NA | 1172 | 1 | AT: 350; AT: 155
20250402 | April | 1030 | 7244 |  |  | 7240 |  |  | 972 | 254 | 722 | Minimum Margin | Validation phase | 718 | 4 | NA | NA | NA | 1190 | 1 | AT: 415; AT: 155
20250402 | April | 1130 | 7243 |  |  | 7239 |  |  | 972 | 253 | 723 | Minimum Margin | Validation phase | 719 | 4 | NA | NA | NA | 1193 | 1 | AT: 415; AT: 155
20250402 | April | 1230 | 8495 |  |  | 8495 |  |  | 1412 | 273 | 1139 | Minimum Margin | TTC Validation phase - bilateral reduction | 1139 | 0 | NA | NA | NA | 2005 | 1 | AT: 415; AT: 155
20250402 | April | 1330 | 8495 |  |  | 8495 |  |  | 1412 | 273 | 1139 | Minimum Margin | TTC Validation phase - bilateral reduction | 1139 | 0 | NA | NA | NA | 2005 | 1 | AT: 438; AT: 155
20250402 | April | 1430 | 8495 |  |  | 8495 |  |  | 1412 | 273 | 1139 | Minimum Margin | TTC Validation phase - bilateral reduction | 1139 | 0 | NA | NA | NA | 2005 | 1 | AT: 438; AT: 155
20250402 | April | 1530 | 8946 |  |  | 8945 |  |  | -1634 | -1634 | -1633 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 438; AT: 155
20250402 | April | 1630 | 8946 |  |  | 8945 |  |  | -1634 | -1634 | -1633 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 1730 | 8946 |  |  | 8945 |  |  | -1634 | -1634 | -1633 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 1830 |  | 8618 | 832 |  | 8408 | 832 | -1810 | -1810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 210 | 0 | 210 | 1810 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 149; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 1930 |  | 8618 | 832 |  | 8408 | 832 | -1810 | -1810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 210 | 0 | 210 | 1810 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 2030 |  | 8618 | 832 |  | 8408 | 832 | -1810 | -1810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 210 | 0 | 210 | 1810 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 2130 | 9592 |  |  | 9307 |  |  | -2312 | -2312 | -2071 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 285 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3230; FR: Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 2230 | 9592 |  |  | 9307 |  |  | -2312 | -2312 | -2071 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 285 | NA | NA | NA | 0 | 1 | AT: 386; AT: 170
20250402 | April | 2330 | 8782 |  |  | 8668 |  |  | -1464 | -1464 | -1368 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 114 | NA | NA | NA | 0 | 1 | AT: 386; AT: 170
20250403 | April | 30 | 7652 |  |  | 7652 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 386; AT: 170
20250403 | April | 130 | 7652 |  |  | 7652 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 359; AT: 170
20250403 | April | 230 | 7652 |  |  | 7652 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 359; AT: 170
20250403 | April | 330 | 7153 |  |  | 7152 |  |  | -2501 | -2501 | -2500 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 359; AT: 170
20250403 | April | 430 | 7153 |  |  | 7152 |  |  | -2501 | -2501 | -2500 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 357; AT: 170
20250403 | April | 530 | 7153 |  |  | 7152 |  |  | -2501 | -2501 | -2500 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250403 | April | 630 | 6953 |  |  | 6952 |  |  | -2298 | -2298 | -2297 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250403 | April | 730 | 8542 |  |  | 8452 |  |  | -4394 | -4394 | -4294 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 90 | NA | NA | NA | 0 | 1 | AT: 400; AT: 155
20250403 | April | 830 | 8542 |  |  | 8500 |  |  | -4394 | -4394 | -4342 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 42 | NA | NA | NA | 0 | 1 | AT: 400; AT: 155
20250403 | April | 930 | 7046 |  |  | 7046 |  |  | -2722 | -2722 | -2721 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 400; AT: 155
20250403 | April | 1030 | 7046 |  |  | 7046 |  |  | -2722 | -2722 | -2721 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250403 | April | 1130 | 7046 |  |  | 7046 |  |  | -2722 | -2722 | -2721 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250403 | April | 1230 | 8136 |  |  | 8119 |  |  | -4732 | -4732 | -4721 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250403 | April | 1330 | 8136 |  |  | 8119 |  |  | -4732 | -4732 | -4721 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 17 | NA | NA | NA | 0 | 1 | AT: 370; AT: 155
20250403 | April | 1430 | 8136 |  |  | 8057 |  |  | -4732 | -4732 | -4658 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 79 | NA | NA | NA | 0 | 1 | AT: 370; AT: 155
20250403 | April | 1530 | 6557 |  |  | 6557 |  |  | -2978 | -2978 | -2977 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 382; AT: 155
20250403 | April | 1630 | 6557 |  |  | 6557 |  |  | -2978 | -2978 | -2977 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 339; AT: 155
20250403 | April | 1730 | 7857 |  |  | 7857 |  |  | -4237 | -4237 | -4237 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 339; AT: 155
20250403 | April | 1830 |  | 6579 | 392 |  | 6578 | 392 | -1854 | -1854 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1854 | 1 | AT: 339; AT: 155
20250403 | April | 1930 |  | 6579 | 392 |  | 6578 | 392 | -1854 | -1854 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1854 | 1 | AT: 339; AT: 155
20250403 | April | 2030 |  | 6579 | 392 |  | 6578 | 392 | -1854 | -1854 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1854 | 1 | AT: 339; AT: 155
20250403 | April | 2130 | 7190 |  |  | 7189 |  |  | -2895 | -2895 | -2895 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 317; AT: 170
20250403 | April | 2230 | 7190 |  |  | 7189 |  |  | -2895 | -2895 | -2895 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0
20250403 | April | 2330 | 6380 |  |  | 6379 |  |  | -2271 | -2271 | -2271 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0
20250404 | April | 30 | 7025 |  |  | 7006 |  |  | 1910 | 196 | 1733 | Minimum Margin | Validation phase | 1714 | 19 | NA | NA | NA | 3270 | 1 | CH: 6756; CH: Reduction due to missing redispatch potential
20250404 | April | 130 | 7025 |  |  | 7006 |  |  | 1910 | 196 | 1733 | Minimum Margin | Validation phase | 1714 | 19 | NA | NA | NA | 3270 | 1 | CH: 6756; CH: Reduction due to missing redispatch potential
20250404 | April | 230 | 7025 |  |  | 7006 |  |  | 1910 | 196 | 1733 | Minimum Margin | Validation phase | 1714 | 19 | NA | NA | NA | 3270 | 1 | CH: 6756; CH: Reduction due to missing redispatch potential
20250404 | April | 330 | 6699 |  |  | 6687 |  |  | 3428 | 219 | 3221 | Minimum Margin | Validation phase | 3209 | 12 | NA | NA | NA | 6223 | 1 | CH: 6437; CH: Reduction due to missing redispatch potential
20250404 | April | 430 | 6699 |  |  | 6687 |  |  | 3428 | 219 | 3221 | Minimum Margin | Validation phase | 3209 | 12 | NA | NA | NA | 6223 | 1 | CH: 6437; CH: Reduction due to missing redispatch potential
20250404 | April | 530 | 6699 |  |  | 6687 |  |  | 3428 | 219 | 3221 | Minimum Margin | Validation phase | 3209 | 12 | NA | NA | NA | 6223 | 1 | CH: 6437; CH: Reduction due to missing redispatch potential; FR: 2536; FR: Process fail during TSO validation phase
20250404 | April | 630 | 6493 |  |  | 6482 |  |  | 3394 | 213 | 3192 | Minimum Margin | Validation phase | 3181 | 11 | NA | NA | NA | 6171 | 1 | CH: 6232; CH: Reduction due to missing redispatch potential; FR: 2536; FR: Process fail during TSO validation phase
20250404 | April | 730 |  | 6584 | 520 |  | 6497 | 520 | 3485 | 202 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3283 | NA | 87 | 0 | 87 | -202 | 0
20250404 | April | 830 |  | 6621 | 523 |  | 6518 | 523 | 3485 | 239 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3246 | NA | 103 | 0 | 103 | -239 | 0
20250404 | April | 930 | 6990 |  |  | 6990 |  |  | -3400 | -3400 | -3400 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250404 | April | 1030 | 6990 |  |  | 6990 |  |  | -3400 | -3400 | -3400 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250404 | April | 1130 | 6990 |  |  | 6990 |  |  | -3400 | -3400 | -3400 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250404 | April | 1230 | 7279 |  |  | 7279 |  |  | -3256 | -3256 | -3256 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250404 | April | 1330 | 7279 |  |  | 7279 |  |  | -3256 | -3256 | -3256 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250404 | April | 1430 | 7279 |  |  | 7279 |  |  | -3256 | -3256 | -3256 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250404 | April | 1530 | 7248 |  |  | 7245 |  |  | 3921 | 258 | 3666 | Minimum Margin | Validation phase | 3663 | 3 | NA | NA | NA | 7074 | 0
20250404 | April | 1630 | 7248 |  |  | 7245 |  |  | 3921 | 258 | 3666 | Minimum Margin | Validation phase | 3663 | 3 | NA | NA | NA | 7074 | 0
20250404 | April | 1730 | 7633 |  |  | 7626 |  |  | 2897 | 243 | 2661 | Minimum Margin | Validation phase | 2654 | 7 | NA | NA | NA | 5079 | 0
20250404 | April | 1830 | 7771 |  |  | 7752 |  |  | 5953 | 181 | 5791 | Minimum Margin | Validation phase | 5772 | 19 | NA | NA | NA | 11401 | 1 | CH: 7502; CH: Reduction due to missing redispatch potential
20250404 | April | 1930 | 7771 |  |  | 7752 |  |  | 5953 | 181 | 5791 | Minimum Margin | Validation phase | 5772 | 19 | NA | NA | NA | 11401 | 1 | CH: 7502; CH: Reduction due to missing redispatch potential
20250404 | April | 2030 | 7771 |  |  | 7752 |  |  | 5953 | 181 | 5791 | Minimum Margin | Validation phase | 5772 | 19 | NA | NA | NA | 11401 | 1 | CH: 7502; CH: Reduction due to missing redispatch potential
20250404 | April | 2130 | 7776 |  |  | 7758 |  |  | 4813 | 186 | 4645 | Minimum Margin | Validation phase | 4627 | 18 | NA | NA | NA | 9104 | 1 | CH: 7508; CH: Reduction due to missing redispatch potential
20250404 | April | 2230 | 7776 |  |  | 7758 |  |  | 4813 | 186 | 4645 | Minimum Margin | Validation phase | 4627 | 18 | NA | NA | NA | 9104 | 1 | CH: 7508; CH: Reduction due to missing redispatch potential
20250404 | April | 2330 | 6956 |  |  | 6940 |  |  | 5025 | 176 | 4865 | Minimum Margin | Validation phase | 4849 | 16 | NA | NA | NA | 9554 | 1 | CH: 6690; CH: Reduction due to missing redispatch potential
20250405 | April | 30 | 6880 |  |  | 6880 |  |  | 437 | 0 | 437 | TTC Selection - LTTC | TTC Selection - LTTC | 437 | 0 | NA | NA | NA | 437 | 0
20250405 | April | 130 | 7081 |  |  | 7068 |  |  | 437 | 201 | 249 | Minimum Margin | Validation phase | 236 | 13 | NA | NA | NA | 297 | 0
20250405 | April | 230 | 7118 |  |  | 7102 |  |  | 437 | 238 | 215 | Minimum Margin | Validation phase | 199 | 16 | NA | NA | NA | 192 | 0
20250405 | April | 330 | 7108 |  |  | 7099 |  |  | 390 | 228 | 171 | Minimum Margin | Validation phase | 162 | 9 | NA | NA | NA | 114 | 0
20250405 | April | 430 | 7103 |  |  | 7094 |  |  | 390 | 223 | 176 | Minimum Margin | Validation phase | 167 | 9 | NA | NA | NA | 129 | 0
20250405 | April | 530 | 7089 |  |  | 7080 |  |  | 390 | 209 | 190 | Minimum Margin | Validation phase | 181 | 9 | NA | NA | NA | 171 | 0
20250405 | April | 630 | 7113 |  |  | 6250 |  |  | 390 | 233 | 1020 | Minimum Margin | Validation phase | 157 | 863 | NA | NA | NA | 1807 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250405 | April | 730 | 7801 |  |  | 5480 |  |  | 677 | 211 | 2787 | Minimum Margin | Validation phase | 466 | 2321 | NA | NA | NA | 5363 | 1 | SI: 6391; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered |  |  | 5230 | Foreseen violations on the border
20250405 | April | 830 | 7796 |  |  | 5480 |  |  | 677 | 206 | 2787 | Minimum Margin | Validation phase | 471 | 2316 | NA | NA | NA | 5368 | 1 | SI: 6388; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered |  |  | 5230 | Foreseen violations on the border
20250405 | April | 930 | 8293 |  |  | 6980 |  |  | -4706 | -4706 | -3393 | Critical Branch | Smoothing ramp | 0 | 1313 | NA | NA | NA | 0 | 1
20250405 | April | 1030 | 8293 |  |  | 8293 |  |  | -4706 | -4706 | -4706 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250405 | April | 1130 | 8293 |  |  | 8293 |  |  | -4706 | -4706 | -4706 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250405 | April | 1230 | 7986 |  |  | 7986 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250405 | April | 1330 | 7986 |  |  | 7986 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 1430 | 7986 |  |  | 7986 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 1530 | 9397 |  |  | 8960 |  |  | -1577 | -1577 | -1208 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 437 | NA | NA | NA | 0 | 1 | FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 1630 | 9397 |  |  | 8960 |  |  | -1577 | -1577 | -1208 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 437 | NA | NA | NA | 0 | 0
20250405 | April | 1730 | 9397 |  |  | 8960 |  |  | -1577 | -1577 | -1208 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 437 | NA | NA | NA | 0 | 0
20250405 | April | 1830 | 7801 |  |  | 7787 |  |  | 869 | 211 | 672 | Minimum Margin | Validation phase | 658 | 14 | NA | NA | NA | 1133 | 0
20250405 | April | 1930 | 7801 |  |  | 7787 |  |  | 869 | 211 | 672 | Minimum Margin | Validation phase | 658 | 14 | NA | NA | NA | 1133 | 0
20250405 | April | 2030 | 7801 |  |  | 7787 |  |  | 869 | 211 | 672 | Minimum Margin | Validation phase | 658 | 14 | NA | NA | NA | 1133 | 0
20250405 | April | 2130 | 7767 |  |  | 7747 |  |  | 666 | 177 | 509 | Minimum Margin | Validation phase | 489 | 20 | NA | NA | NA | 841 | 0
20250405 | April | 2230 | 7767 |  |  | 7747 |  |  | 666 | 177 | 509 | Minimum Margin | Validation phase | 489 | 20 | NA | NA | NA | 841 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 2330 | 6947 |  |  | 6929 |  |  | 1080 | 167 | 931 | Minimum Margin | Validation phase | 913 | 18 | NA | NA | NA | 1695 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 30 | 9209 |  |  | 8646 |  |  | -4347 | -4347 | -3603 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 563 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 130 | 9209 |  |  | 8646 |  |  | -4347 | -4347 | -3603 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 563 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 230 | 9209 |  |  | 8646 |  |  | -4347 | -4347 | -3603 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 563 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 330 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 324 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 430 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 324 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 530 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 324 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20250406 | April | 630 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 324 | NA | NA | NA | 0 | 1 | AT: 402; AT: 170
20250406 | April | 730 | 8323 |  |  | 8322 |  |  | -5552 | -5552 | -5551 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 830 | 8323 |  |  | 8322 |  |  | -5552 | -5552 | -5551 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 930 | 8743 |  |  | 8394 |  |  | -1336 | -1336 | -1037 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 424; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1030 | 8743 |  |  | 8394 |  |  | -1336 | -1336 | -1037 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 407; AT: 170
20250406 | April | 1130 | 8743 |  |  | 8394 |  |  | -1336 | -1336 | -1037 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 349 | NA | NA | NA | 0 | 1 | AT: 407; AT: 170
20250406 | April | 1230 | 8421 |  |  | 8420 |  |  | -1423 | -1423 | -1423 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 400; AT: 170
20250406 | April | 1330 | 8421 |  |  | 8420 |  |  | -1423 | -1423 | -1423 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 323; AT: 170
20250406 | April | 1430 | 8421 |  |  | 7750 |  |  | -1423 | -1423 | -753 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 671 | NA | NA | NA | 0 | 1 | AT: 323; AT: 170
20250406 | April | 1530 |  | 6266 | 418 |  | 5974 | 418 | -4347 | -4347 | 0 | TTC Selection - LTTCImport and LTTCExport | Validation phase | 0 | NA | 292 | 0 | 292 | 4347 | 1 | AT: 323; AT: 170
20250406 | April | 1630 |  | 6266 | 418 |  | 5974 | 418 | -4347 | -4347 | 0 | TTC Selection - LTTCImport and LTTCExport | Validation phase | 0 | NA | 292 | 0 | 292 | 4347 | 1 | AT: 400; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1730 |  | 6266 | 418 |  | 5974 | 418 | -4347 | -4347 | 0 | TTC Selection - LTTCImport and LTTCExport | Validation phase | 0 | NA | 292 | 0 | 292 | 4347 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1830 | 9008 |  |  | 7750 |  |  | -5645 | -5645 | -4393 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1258 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1930 | 9008 |  |  | 8542 |  |  | -5645 | -5645 | -5196 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 466 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 2030 | 9008 |  |  | 8542 |  |  | -5645 | -5645 | -5196 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 466 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 2130 | 8688 |  |  | 8362 |  |  | -5634 | -5634 | -5320 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 421; AT: 170; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 2230 | 8688 |  |  | 8362 |  |  | -5634 | -5634 | -5320 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 169; AT: Reduction because NTC over thermal limit on border
20250406 | April | 2330 | 8688 |  |  | 8362 |  |  | -5634 | -5634 | -5320 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 326 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 169; AT: Reduction because NTC over thermal limit on border
20250407 | April | 30 |  | 7812 | 734 |  | 7803 | 734 | -865 | -865 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 9 | 0 | 9 | 865 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 169; AT: Reduction because NTC over thermal limit on border
20250407 | April | 130 |  | 7812 | 734 |  | 7803 | 734 | -865 | -865 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 9 | 0 | 9 | 865 | 1 | AT: 424; AT: 170; FR: 2975; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 230 |  | 7812 | 734 |  | 7803 | 734 | -865 | -865 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 9 | 0 | 9 | 865 | 1 | AT: 424; AT: 170; FR: 2975; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 330 |  | 7501 | 734 |  | 7493 | 734 | 335 | 179 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 156 | NA | 8 | 0 | 8 | -179 | 1 | AT: 424; AT: 170; FR: 2975; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 430 |  | 7501 | 734 |  | 7493 | 734 | 335 | 179 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 156 | NA | 8 | 0 | 8 | -179 | 1 | AT: 425; AT: 170; FR: 2975; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 530 |  | 7501 | 734 |  | 7493 | 734 | 335 | 179 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 156 | NA | 8 | 0 | 8 | -179 | 1 | AT: 432; AT: 153; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 630 |  | 7335 | 737 |  | 7322 | 737 | 343 | 213 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 130 | NA | 13 | 0 | 13 | -213 | 1 | AT: 432; AT: 153; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 730 |  | 8098 | 732 |  | 7999 | 732 | -4363 | -4363 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 99 | 0 | 99 | 4363 | 1 | AT: 337; AT: 155; FR: 2480; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 830 |  | 8098 | 732 |  | 7999 | 732 | -4363 | -4363 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 99 | 0 | 99 | 4363 | 1 | AT: 337; AT: 155; FR: 2480; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 930 | 7040 |  |  | 6940 |  |  | -3573 | -3573 | -3480 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 100 | NA | NA | NA | 0 | 1 | AT: 337; AT: 155; FR: 2480; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1030 | 7040 |  |  | 6940 |  |  | -3573 | -3573 | -3480 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 100 | NA | NA | NA | 0 | 1 | AT: 384; AT: 155; FR: 2837; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1130 | 7040 |  |  | 6940 |  |  | -3573 | -3573 | -3480 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 100 | NA | NA | NA | 0 | 1 | AT: 384; AT: 155; FR: 2837; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1230 | 7946 |  |  | 6117 |  |  | -1266 | -1266 | 563 | Critical Branch | Validation phase | 0 | 1829 | NA | NA | NA | 2392 | 1 | AT: 384; AT: 155; FR: 2837; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1330 | 7946 |  |  | 6117 |  |  | -1266 | -1266 | 563 | Critical Branch | Validation phase | 0 | 1829 | NA | NA | NA | 2392 | 1 | AT: 348; AT: 155; FR: 2563; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1430 | 7946 |  |  | 6117 |  |  | -1266 | -1266 | 563 | Critical Branch | Validation phase | 0 | 1829 | NA | NA | NA | 2392 | 1 | AT: 348; AT: 155; FR: 2563; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1530 | 7250 |  |  | 7150 |  |  | -3448 | -3448 | -3356 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 100 | NA | NA | NA | 0 | 1 | AT: 348; AT: 155; FR: 2563; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1630 | 7250 |  |  | 7150 |  |  | -3448 | -3448 | -3356 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 100 | NA | NA | NA | 0 | 1 | AT: 208; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1730 | 7250 |  |  | 7150 |  |  | -3448 | -3448 | -3356 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 100 | NA | NA | NA | 0 | 1 | AT: 215; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1830 |  | 8394 | 947 |  | 8016 | 935 | -4370 | -4370 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 378 | 12 | 390 | 4370 | 1 | AT: 215; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1930 |  | 8394 | 947 |  | 8046 | 935 | -4370 | -4370 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 348 | 12 | 360 | 4370 | 1 | AT: 402; AT: 149
20250407 | April | 2030 |  | 8394 | 947 |  | 8046 | 935 | -4370 | -4370 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 348 | 12 | 360 | 4370 | 1 | AT: 402; AT: 149
20250407 | April | 2130 |  | 7752 | 831 |  | 7752 | 831 | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 997 | 1 | AT: 381; AT: 164
20250407 | April | 2230 |  | 7752 | 831 |  | 7752 | 831 | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 997 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 161; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 2330 |  | 6997 | 851 |  | 6997 | 851 | -106 | -106 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 106 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 161; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250408 | April | 30 |  | 9039 | 913 |  | 8392 | 913 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 647 | 0 | 647 | 3169 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 161; AT: Reduction because NTC over thermal limit on border; FR: 3200; FR: Planned outage of Creys-Saint-Vulbas 2
20250408 | April | 130 |  | 9039 | 913 |  | 8392 | 913 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 647 | 0 | 647 | 3169 | 1 | AT: 390; AT: 170
20250408 | April | 230 |  | 9039 | 913 |  | 8392 | 913 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 647 | 0 | 647 | 3169 | 1 | AT: 390; AT: 170
20250408 | April | 330 |  | 7163 | 665 |  | 7162 | 665 | 2086 | 222 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1864 | NA | 1 | 0 | 1 | -222 | 1 | AT: 390; AT: 170
20250408 | April | 430 |  | 7163 | 665 |  | 7162 | 665 | 2086 | 222 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1864 | NA | 1 | 0 | 1 | -222 | 1 | AT: 377; AT: 170
20250408 | April | 530 |  | 7163 | 665 |  | 7162 | 665 | 2086 | 222 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1864 | NA | 1 | 0 | 1 | -222 | 1 | AT: 187; AT: 136
20250408 | April | 630 |  | 6767 | 647 |  | 6766 | 647 | 2112 | 25 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2087 | NA | 1 | 0 | 1 | -25 | 1 | AT: 187; AT: 136
20250408 | April | 730 |  | 7175 | 787 |  | 7175 | 786 | -4319 | -4319 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 4319 | 1 | AT: 450; AT: 155
20250408 | April | 830 |  | 7175 | 787 |  | 7175 | 786 | -4319 | -4319 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 4319 | 1 | AT: 450; AT: 155
20250408 | April | 930 | 9210 |  |  | 9210 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 428; AT: 155
20250408 | April | 1030 | 9210 |  |  | 9210 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 351; AT: 155
20250408 | April | 1130 | 9210 |  |  | 8796 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 414 | NA | NA | NA | 0 | 1 | AT: 351; AT: 155
20250408 | April | 1230 | 7296 |  |  | 7296 |  |  | 8747 | 256 | 8491 | Minimum Margin | TTC Validation phase - bilateral reduction | 8491 | 0 | NA | NA | NA | 16726 | 1 | AT: 351; AT: 155
20250408 | April | 1330 | 7296 |  |  | 7296 |  |  | 8747 | 256 | 8491 | Minimum Margin | TTC Validation phase - bilateral reduction | 8491 | 0 | NA | NA | NA | 16726 | 1 | AT: 428; AT: 155
20250408 | April | 1430 | 7295 |  |  | 7295 |  |  | 8747 | 255 | 8492 | Minimum Margin | TTC Validation phase - bilateral reduction | 8492 | 0 | NA | NA | NA | 16729 | 1 | AT: 450; AT: 155
20250408 | April | 1530 | 9210 |  |  | 7976 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250408 | April | 1630 | 9210 |  |  | 7976 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 196; AT: 138
20250408 | April | 1730 | 9210 |  |  | 7976 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1234 | NA | NA | NA | 0 | 1 | AT: 196; AT: 136
20250408 | April | 1830 |  | 7506 | 793 |  | 7506 | 793 | 6744 | 174 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 6570 | NA | 0 | 0 | 0 | -174 | 1 | AT: 196; AT: 138
20250408 | April | 1930 |  | 7441 | 787 |  | 7441 | 786 | 6744 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 6635 | NA | 0 | 1 | 1 | -109 | 1 | AT: 429; AT: 155
20250408 | April | 2030 |  | 7523 | 795 |  | 7523 | 795 | 6744 | 191 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 6553 | NA | 0 | 0 | 0 | -191 | 1 | AT: 429; AT: 155
20250408 | April | 2130 |  | 8245 | 680 |  | 8244 | 680 | -2758 | -2758 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2758 | 1 | AT: 410; AT: 170
20250408 | April | 2230 |  | 8245 | 680 |  | 8244 | 680 | -2758 | -2758 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2758 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250408 | April | 2330 |  | 7492 | 700 |  | 7492 | 700 | -1906 | -1906 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1906 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 30 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 130 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 0
20250409 | April | 230 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 0
20250409 | April | 330 | 6530 |  |  | 6530 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250409 | April | 430 | 6530 |  |  | 6530 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250409 | April | 530 | 6530 |  |  | 6530 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250409 | April | 630 | 6330 |  |  | 6330 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250409 | April | 730 |  | 6146 | 579 |  | 6146 | 579 | 7943 | 78 | 0 | Minimum Margin | Minimum Margin | 7865 | NA | 0 | 0 | 0 | -78 | 0
20250409 | April | 830 |  | 6146 | 579 |  | 6146 | 579 | 7943 | 78 | 0 | Minimum Margin | Minimum Margin | 7865 | NA | 0 | 0 | 0 | -78 | 0
20250409 | April | 930 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250409 | April | 1030 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1130 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1230 | 9210 |  |  | 7450 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1760 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2; SI: 7433; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250409 | April | 1330 | 9210 |  |  | 7450 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1760 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2; SI: 7433; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250409 | April | 1430 | 9210 |  |  | 7450 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1760 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2; SI: 7433; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250409 | April | 1530 | 9210 |  |  | 8375 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1630 | 9210 |  |  | 8375 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1730 | 9210 |  |  | 8375 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1830 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1930 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2030 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2130 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2230 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2330 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 30 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 130 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 230 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 330 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 430 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 530 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 0
20250410 | April | 630 | 8400 |  |  | 7712 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 0 | 0
20250410 | April | 730 |  | 6434 | 395 |  | 5926 | 395 | 6894 | 2 | 0 | Minimum Margin | Validation phase | 6892 | NA | 508 | 0 | 508 | -2 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250410 | April | 830 |  | 6649 | 413 |  | 6142 | 413 | 6894 | 218 | 0 | Minimum Margin | Validation phase | 6676 | NA | 507 | 0 | 507 | -218 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250410 | April | 930 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250410 | April | 1030 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1130 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1230 | 8254 |  |  | 7787 |  |  | 5989 | 214 | 6878 | Minimum Margin | Validation phase | 5775 | 467 | NA | NA | NA | 13542 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1330 | 8254 |  |  | 7787 |  |  | 5989 | 214 | 6878 | Minimum Margin | Validation phase | 5775 | 467 | NA | NA | NA | 13542 | 0
20250410 | April | 1430 | 8254 |  |  | 7787 |  |  | 5989 | 214 | 6878 | Minimum Margin | Validation phase | 5775 | 467 | NA | NA | NA | 13542 | 0
20250410 | April | 1530 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250410 | April | 1630 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1730 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1830 | 9410 |  |  | 8540 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 870 | NA | NA | NA | 0 | 1 | FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1930 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 0
20250410 | April | 2030 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 835 | NA | NA | NA | 0 | 0
20250410 | April | 2130 | 7486 |  |  | 7479 |  |  | 5684 | 246 | 5445 | Minimum Margin | Validation phase | 5438 | 7 | NA | NA | NA | 10644 | 0
20250410 | April | 2230 | 7489 |  |  | 7482 |  |  | 5684 | 249 | 5442 | Minimum Margin | Validation phase | 5435 | 7 | NA | NA | NA | 10635 | 1 | AT: 338; AT: 170
20250410 | April | 2330 | 6664 |  |  | 6658 |  |  | 5905 | 234 | 5677 | Minimum Margin | Validation phase | 5671 | 6 | NA | NA | NA | 11120 | 1 | AT: 338; AT: 170
20250411 | April | 30 | 7080 |  |  | 7059 |  |  | 2688 | 200 | 2509 | Minimum Margin | Validation phase | 2488 | 21 | NA | NA | NA | 4818 | 1 | AT: 337; AT: 170
20250411 | April | 130 | 7069 |  |  | 7049 |  |  | 2688 | 189 | 2519 | Minimum Margin | Validation phase | 2499 | 20 | NA | NA | NA | 4849 | 1 | AT: 414; AT: 170; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 230 | 7047 |  |  | 7030 |  |  | 2688 | 167 | 2538 | Minimum Margin | Validation phase | 2521 | 17 | NA | NA | NA | 4909 | 1 | AT: 435; AT: 170; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 330 | 8950 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1038 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 430 | 8950 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1038 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 530 | 8950 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1038 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 630 | 8750 |  |  | 7712 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1038 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 730 | 9560 |  |  | 7003 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2557 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 830 | 9560 |  |  | 7003 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2557 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 930 | 9560 |  |  | 7555 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2005 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1030 | 9560 |  |  | 7555 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2005 | NA | NA | NA | 0 | 1 | AT: -155; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1130 | 9560 |  |  | 7555 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2005 | NA | NA | NA | 0 | 1 | AT: 62; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1230 | 8123 |  |  | 7531 |  |  | 4398 | 204 | 5526 | Minimum Margin | Validation phase | 4194 | 592 | NA | NA | NA | 10848 | 1 | AT: 377; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border; FR: 2600; FR: Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1330 | 8123 |  |  | 7531 |  |  | 4398 | 204 | 5526 | Minimum Margin | Validation phase | 4194 | 592 | NA | NA | NA | 10848 | 1 | AT: 260; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 1430 | 8123 |  |  | 7531 |  |  | 4398 | 204 | 5526 | Minimum Margin | Validation phase | 4194 | 592 | NA | NA | NA | 10848 | 1 | AT: 342; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 1530 | 7390 |  |  | 7390 |  |  | -3804 | -3804 | -3804 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 347; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 1630 | 7390 |  |  | 7390 |  |  | -3804 | -3804 | -3804 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 355; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 1730 | 7890 |  |  | 7890 |  |  | -4290 | -4290 | -4290 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 357; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 1830 |  | 7573 | 489 |  | 7573 | 489 | 3464 | 107 | 0 | Minimum Margin | Minimum Margin | 3357 | NA | 0 | 0 | 0 | -107 | 1 | AT: 360; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 1930 |  | 7610 | 492 |  | 7610 | 492 | 3464 | 144 | 0 | Minimum Margin | Minimum Margin | 3320 | NA | 0 | 0 | 0 | -144 | 1 | AT: 356; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 2030 |  | 7672 | 496 |  | 7672 | 496 | 3464 | 207 | 0 | Minimum Margin | Minimum Margin | 3257 | NA | 0 | 0 | 0 | -207 | 1 | AT: 299; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250411 | April | 2130 | 8252 |  |  | 8235 |  |  | 3499 | 162 | 3354 | Minimum Margin | Validation phase | 3337 | 17 | NA | NA | NA | 6546 | 1 | AT: 338; AT: 170
20250411 | April | 2230 | 8287 |  |  | 8267 |  |  | 3499 | 197 | 3322 | Minimum Margin | Validation phase | 3302 | 20 | NA | NA | NA | 6447 | 0
20250411 | April | 2330 | 7454 |  |  | 7438 |  |  | 3756 | 174 | 3598 | Minimum Margin | Validation phase | 3582 | 16 | NA | NA | NA | 7022 | 0
20250412 | April | 30 | 8297 |  |  | 8297 |  |  | -4457 | -4457 | -4457 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 130 | 8297 |  |  | 8297 |  |  | -4457 | -4457 | -4457 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 230 | 8297 |  |  | 8297 |  |  | -4457 | -4457 | -4457 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 330 | 7610 |  |  | 7595 |  |  | 3216 | 230 | 3001 | Minimum Margin | Validation phase | 2986 | 15 | NA | NA | NA | 5772 | 0
20250412 | April | 430 | 7553 |  |  | 7542 |  |  | 3216 | 173 | 3054 | Minimum Margin | Validation phase | 3043 | 11 | NA | NA | NA | 5935 | 0
20250412 | April | 530 | 7599 |  |  | 7585 |  |  | 3216 | 219 | 3011 | Minimum Margin | Validation phase | 2997 | 14 | NA | NA | NA | 5803 | 0
20250412 | April | 630 | 7598 |  |  | 7584 |  |  | 3216 | 218 | 3012 | Minimum Margin | Validation phase | 2998 | 14 | NA | NA | NA | 5806 | 0
20250412 | April | 730 | 8090 |  |  | 7603 |  |  | -4067 | -4067 | -3580 | TTC Selection - LTTC | Validation phase | 0 | 487 | NA | NA | NA | 0 | 1 | [28 empty] | 7353 | Foreseen violations on the border
20250412 | April | 830 | 8090 |  |  | 7603 |  |  | -4067 | -4067 | -3580 | TTC Selection - LTTC | Validation phase | 0 | 487 | NA | NA | NA | 0 | 1 | [28 empty] | 7353 | Foreseen violations on the border
20250412 | April | 930 | 9277 |  |  | 9103 |  |  | -3733 | -3733 | -3559 | Critical Branch | Smoothing ramp | 0 | 174 | NA | NA | NA | 0 | 1
20250412 | April | 1030 | 9277 |  |  | 9206 |  |  | -3733 | -3733 | -3662 | Critical Branch | Validation phase | 0 | 71 | NA | NA | NA | 0 | 0
20250412 | April | 1130 | 9277 |  |  | 9206 |  |  | -3733 | -3733 | -3662 | Critical Branch | Validation phase | 0 | 71 | NA | NA | NA | 0 | 0
20250412 | April | 1230 | 8546 |  |  | 8546 |  |  | -2007 | -2007 | -2007 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 1330 | 8546 |  |  | 8546 |  |  | -2007 | -2007 | -2007 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 1430 | 8546 |  |  | 8546 |  |  | -2007 | -2007 | -2007 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 1530 | 10260 |  |  | 9397 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 863 | NA | NA | NA | 0 | 1 | SI: 9147; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250412 | April | 1630 | 10260 |  |  | 9397 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 863 | NA | NA | NA | 0 | 1 | SI: 9147; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250412 | April | 1730 | 10260 |  |  | 8197 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2063 | NA | NA | NA | 0 | 1 | SI: 9147; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered |  |  | 7947 | Foreseen violations on the border
20250412 | April | 1830 | 8328 |  |  | 8310 |  |  | 3341 | 131 | 3228 | Minimum Margin | Validation phase | 3210 | 18 | NA | NA | NA | 6325 | 0
20250412 | April | 1930 | 8414 |  |  | 8383 |  |  | 3341 | 217 | 3155 | Minimum Margin | Validation phase | 3124 | 31 | NA | NA | NA | 6093 | 0
20250412 | April | 2030 | 8385 |  |  | 8358 |  |  | 3341 | 188 | 3180 | Minimum Margin | Validation phase | 3153 | 27 | NA | NA | NA | 6172 | 0
20250412 | April | 2130 | 8444 |  |  | 8444 |  |  | -3683 | -3683 | -3683 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 2230 | 8444 |  |  | 8444 |  |  | -3683 | -3683 | -3683 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250412 | April | 2330 | 7634 |  |  | 7634 |  |  | -2940 | -2940 | -2940 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 30 | 8347 |  |  | 8347 |  |  | -4650 | -4650 | -4650 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 130 | 8347 |  |  | 8347 |  |  | -4650 | -4650 | -4650 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 230 | 8347 |  |  | 8347 |  |  | -4650 | -4650 | -4650 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 330 | 8119 |  |  | 8119 |  |  | -4054 | -4054 | -4054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 430 | 8119 |  |  | 8119 |  |  | -4054 | -4054 | -4054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 530 | 8119 |  |  | 8119 |  |  | -4054 | -4054 | -4054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 630 | 8119 |  |  | 8119 |  |  | -4054 | -4054 | -4054 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 730 | 8475 |  |  | 8475 |  |  | -4957 | -4957 | -4957 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 830 | 8475 |  |  | 8475 |  |  | -4957 | -4957 | -4957 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250413 | April | 930 | 8975 |  |  | 7517 |  |  | -1276 | -1276 | 182 | Critical Branch | Validation phase | 0 | 1458 | NA | NA | NA | 1640 | 1 | CH: 7267; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1030 | 8975 |  |  | 7517 |  |  | -1276 | -1276 | 182 | Critical Branch | Validation phase | 0 | 1458 | NA | NA | NA | 1640 | 1 | CH: 7267; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1130 | 8975 |  |  | 7517 |  |  | -1276 | -1276 | 182 | Critical Branch | Validation phase | 0 | 1458 | NA | NA | NA | 1640 | 1 | CH: 7267; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1230 | 8486 |  |  | 7479 |  |  | -440 | -440 | 567 | Critical Branch | Validation phase | 0 | 1007 | NA | NA | NA | 1574 | 1 | CH: 7229; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1330 | 8486 |  |  | 7479 |  |  | -440 | -440 | 567 | Critical Branch | Validation phase | 0 | 1007 | NA | NA | NA | 1574 | 1 | CH: 7229; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1430 | 8486 |  |  | 7479 |  |  | -440 | -440 | 567 | Critical Branch | Validation phase | 0 | 1007 | NA | NA | NA | 1574 | 1 | CH: 7229; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1530 | 9289 |  |  | 8015 |  |  | -1601 | -1601 | -327 | Critical Branch | Validation phase | 0 | 1274 | NA | NA | NA | 0 | 1 | CH: 7765; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250413 | April | 1630 | 9589 |  |  | 8315 |  |  | -1944 | -1944 | -670 | Critical Branch | Validation phase | 0 | 1274 | NA | NA | NA | 0 | 1 | CH: 8065; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3463; FR: Process fail during TSO validation phase
20250413 | April | 1730 | 9589 |  |  | 8315 |  |  | -1944 | -1944 | -670 | Critical Branch | Validation phase | 0 | 1274 | NA | NA | NA | 0 | 1 | CH: 8065; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3463; FR: Process fail during TSO validation phase
20250413 | April | 1830 |  | 7840 | 618 |  | 7758 | 618 | 2818 | 169 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2649 | NA | 82 | 0 | 82 | -169 | 1 | FR: 3463; FR: Process fail during TSO validation phase
20250413 | April | 1930 |  | 7888 | 622 |  | 7783 | 622 | 2818 | 217 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2601 | NA | 105 | 0 | 105 | -217 | 0
20250413 | April | 2030 |  | 7777 | 613 |  | 7726 | 613 | 2818 | 106 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2712 | NA | 51 | 0 | 51 | -106 | 0
20250413 | April | 2130 | 8403 |  |  | 8397 |  |  | 4720 | 56 | 4670 | Minimum Margin | Validation phase | 4664 | 6 | NA | NA | NA | 9284 | 1 | CH: 8147; CH: Reduction due to missing redispatch potential
20250413 | April | 2230 | 8525 |  |  | 8505 |  |  | 4720 | 178 | 4562 | Minimum Margin | Validation phase | 4542 | 20 | NA | NA | NA | 8946 | 1 | CH: 8255; CH: Reduction due to missing redispatch potential
20250413 | April | 2330 | 8499 |  |  | 8482 |  |  | 4720 | 152 | 4585 | Minimum Margin | Validation phase | 4568 | 17 | NA | NA | NA | 9018 | 1 | CH: 8232; CH: Reduction due to missing redispatch potential
20250414 | April | 30 | 8482 |  |  | 8482 |  |  | -3672 | -3672 | -3672 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250414 | April | 130 | 8482 |  |  | 8482 |  |  | -3672 | -3672 | -3672 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250414 | April | 230 | 8482 |  |  | 8482 |  |  | -3672 | -3672 | -3672 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250414 | April | 330 |  | 7833 | 625 |  | 7833 | 625 | -3353 | -3353 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3353 | 0
20250414 | April | 430 |  | 7833 | 625 |  | 7833 | 625 | -3353 | -3353 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3353 | 0
20250414 | April | 530 |  | 7833 | 625 |  | 7833 | 625 | -3353 | -3353 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 3353 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 630 |  | 7633 | 625 |  | 7216 | 625 | -3182 | -3182 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 417 | 0 | 417 | 3182 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 730 | 7490 |  |  | 6000 |  |  | -1255 | -1255 | 593 | TTC Selection - LTTC | Validation phase | 0 | 1490 | NA | NA | NA | 2441 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250414 | April | 830 | 7290 |  |  | 5949 |  |  | -1180 | -1180 | 574 | TTC Selection - LTTC | Validation phase | 0 | 1341 | NA | NA | NA | 2328 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250414 | April | 930 | 7290 |  |  | 6573 |  |  | -838 | -838 | 864 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 717 | NA | NA | NA | 2566 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1030 | 7290 |  |  | 6573 |  |  | -838 | -838 | 864 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 717 | NA | NA | NA | 2566 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1130 | 7290 |  |  | 6573 |  |  | -838 | -838 | 864 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 717 | NA | NA | NA | 2566 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1230 | 7376 |  |  | 5736 |  |  | -2705 | -2705 | -1077 | Critical Branch | Validation phase | 0 | 1640 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1330 | 7376 |  |  | 5736 |  |  | -2705 | -2705 | -1077 | Critical Branch | Validation phase | 0 | 1640 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1430 | 7376 |  |  | 5736 |  |  | -2705 | -2705 | -1077 | Critical Branch | Validation phase | 0 | 1640 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1530 | 7371 |  |  | 6622 |  |  | -2642 | -2642 | -869 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 749 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1630 | 7371 |  |  | 6622 |  |  | -2642 | -2642 | -869 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 749 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1730 | 7371 |  |  | 6622 |  |  | -2642 | -2642 | -869 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 749 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1830 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1930 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2030 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2130 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2230 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 30 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 130 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 230 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 430 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 530 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 630 | 8650 |  |  | 7212 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 730 | 9460 |  |  | 6434 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3026 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6808; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 830 | 9460 |  |  | 6434 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3026 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6808; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 930 | 9460 |  |  | 6708 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2752 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7264; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1030 | 9460 |  |  | 6708 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2752 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7264; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1130 | 9460 |  |  | 6708 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2752 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7264; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1230 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2210 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8168; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1330 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2210 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8168; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1430 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2210 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8168; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1530 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2211 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8166; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1630 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2211 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8166; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1730 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2211 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8166; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1830 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 1930 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2030 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2130 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2230 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 30 | 7045 |  |  | 6345 |  |  | 2149 | 222 | 3535 | Minimum Margin | Validation phase | 1927 | 700 | NA | NA | NA | 6848 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 130 | 7045 |  |  | 6345 |  |  | 2149 | 222 | 3535 | Minimum Margin | Validation phase | 1927 | 700 | NA | NA | NA | 6848 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 230 | 7045 |  |  | 6345 |  |  | 2149 | 222 | 3535 | Minimum Margin | Validation phase | 1927 | 700 | NA | NA | NA | 6848 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 330 | 7003 |  |  | 6320 |  |  | 2989 | 223 | 4331 | Minimum Margin | Validation phase | 2766 | 683 | NA | NA | NA | 8439 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 430 | 7003 |  |  | 6320 |  |  | 2989 | 223 | 4331 | Minimum Margin | Validation phase | 2766 | 683 | NA | NA | NA | 8439 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 530 | 7003 |  |  | 6320 |  |  | 2989 | 223 | 4331 | Minimum Margin | Validation phase | 2766 | 683 | NA | NA | NA | 8439 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 630 | 6648 |  |  | 6053 |  |  | 2967 | 68 | 4237 | Minimum Margin | Validation phase | 2899 | 595 | NA | NA | NA | 8406 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 730 | 7315 |  |  | 6588 |  |  | 3420 | 25 | 5119 | Minimum Margin | Validation phase | 3395 | 727 | NA | NA | NA | 10213 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 830 | 7542 |  |  | 6720 |  |  | 3420 | 252 | 5108 | Minimum Margin | Validation phase | 3168 | 822 | NA | NA | NA | 9964 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 930 | 7542 |  |  | 6723 |  |  | 1972 | 252 | 3662 | Minimum Margin | Validation phase | 1720 | 819 | NA | NA | NA | 7072 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1030 | 7545 |  |  | 6725 |  |  | 1972 | 255 | 3662 | Minimum Margin | Validation phase | 1717 | 820 | NA | NA | NA | 7069 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1130 | 7543 |  |  | 6724 |  |  | 1972 | 253 | 3662 | Minimum Margin | Validation phase | 1719 | 819 | NA | NA | NA | 7071 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1230 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2210 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8168; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1330 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2210 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8168; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1430 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2210 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8168; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1530 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2211 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8166; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1630 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2211 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8166; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1730 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2211 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8166; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1830 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1930 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2030 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2130 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2230 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 30 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1238 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 130 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1238 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 230 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1238 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 330 | 6780 |  |  | 6403 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 377 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 430 | 6780 |  |  | 6403 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 377 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 530 | 6780 |  |  | 6403 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 377 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 630 | 6580 |  |  | 6224 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 356 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 730 | 9460 |  |  | 7302 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2158 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7828; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 830 | 9460 |  |  | 7302 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2158 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7828; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 930 | 9460 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2035 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8035; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1030 | 9460 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2035 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8035; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1130 | 9460 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2035 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8035; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1230 | 7290 |  |  | 6212 |  |  | -3141 | -3141 | -1896 | TTC Selection - LTTC | Validation phase | 0 | 1078 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1330 | 7290 |  |  | 6212 |  |  | -3141 | -3141 | -1896 | TTC Selection - LTTC | Validation phase | 0 | 1078 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1430 | 7290 |  |  | 6212 |  |  | -3141 | -3141 | -1896 | TTC Selection - LTTC | Validation phase | 0 | 1078 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1530 | 9460 |  |  | 7478 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8123; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1630 | 9460 |  |  | 7478 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8123; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1730 | 9460 |  |  | 7478 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1982 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8123; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1830 | 7515 |  |  | 6977 |  |  | 2792 | 25 | 4060 | Minimum Margin | TTC Validation phase - bilateral reduction | 2767 | 538 | NA | NA | NA | 8095 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 1930 | 7523 |  |  | 6982 |  |  | 2792 | 33 | 4059 | Minimum Margin | Validation phase | 2759 | 541 | NA | NA | NA | 8085 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2030 | 7525 |  |  | 6983 |  |  | 2792 | 35 | 4059 | Minimum Margin | Validation phase | 2757 | 542 | NA | NA | NA | 8083 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2130 | 7490 |  |  | 6962 |  |  | -924 | -924 | 349 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 528 | NA | NA | NA | 1622 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2230 | 7490 |  |  | 6962 |  |  | -924 | -924 | 349 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 528 | NA | NA | NA | 1622 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2330 | 6680 |  |  | 6344 |  |  | -409 | -409 | 364 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 336 | NA | NA | NA | 1137 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 30 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1238 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 130 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1238 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 230 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1238 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 330 | 7006 |  |  | 6530 |  |  | 2400 | 226 | 3257 | Minimum Margin | Validation phase | 2174 | 476 | NA | NA | NA | 6288 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 430 | 7006 |  |  | 6530 |  |  | 2400 | 226 | 3257 | Minimum Margin | Validation phase | 2174 | 476 | NA | NA | NA | 6288 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 530 | 7006 |  |  | 6530 |  |  | 2400 | 226 | 3257 | Minimum Margin | Validation phase | 2174 | 476 | NA | NA | NA | 6288 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 630 | 7006 |  |  | 6140 |  |  | 2400 | 226 | 3287 | Minimum Margin | Validation phase | 2174 | 866 | NA | NA | NA | 6348 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 730 | 7430 |  |  | 6335 |  |  | 4160 | 240 | 5015 | Minimum Margin | Validation phase | 3920 | 1095 | NA | NA | NA | 9790 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 830 | 7430 |  |  | 6335 |  |  | 4160 | 240 | 5015 | Minimum Margin | Validation phase | 3920 | 1095 | NA | NA | NA | 9790 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 930 | 9360 |  |  | 7624 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1736 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7985; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1030 | 9360 |  |  | 7568 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1792 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7895; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1130 | 9360 |  |  | 7568 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1792 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7895; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1230 | 9360 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3025 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1330 | 9360 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3025 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1430 | 9360 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3025 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1530 | 9660 |  |  | 7520 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | FR: 2200; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 8223; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1630 | 9660 |  |  | 7520 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | SI: 8223; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1730 | 10360 |  |  | 7181 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3179 | NA | NA | NA | 0 | 1 | SI: 8573; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1830 | 10360 |  |  | 8412 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1948 | NA | NA | NA | 0 | 0
20250418 | April | 1930 | 10360 |  |  | 8412 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1948 | NA | NA | NA | 0 | 0
20250418 | April | 2030 | 10360 |  |  | 8412 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1948 | NA | NA | NA | 0 | 0
20250418 | April | 2130 | 8415 |  |  | 8412 |  |  | 1591 | 225 | 1369 | Minimum Margin | Validation phase | 1366 | 3 | NA | NA | NA | 2513 | 0
20250418 | April | 2230 | 8415 |  |  | 8412 |  |  | 1591 | 225 | 1369 | Minimum Margin | Validation phase | 1366 | 3 | NA | NA | NA | 2513 | 0
20250418 | April | 2330 | 7594 |  |  | 7591 |  |  | 1966 | 214 | 1755 | Minimum Margin | Validation phase | 1752 | 3 | NA | NA | NA | 3296 | 0
20250419 | April | 30 | 8950 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250419 | April | 130 | 8950 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250419 | April | 230 | 8950 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250419 | April | 330 | 8950 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250419 | April | 430 | 8950 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250419 | April | 530 | 8950 |  |  | 8335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 615 | NA | NA | NA | 0 | 1
20250419 | April | 630 | 8950 |  |  | 6835 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 2115 | NA | NA | NA | 0 | 1
20250419 | April | 730 | 9760 |  |  | 5335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 4425 | NA | NA | NA | 0 | 1
20250419 | April | 830 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 930 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1030 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1130 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1230 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1330 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1430 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1530 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1630 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1730 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1830 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5925 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1930 | 9760 |  |  | 5335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 4425 | NA | NA | NA | 0 | 1
20250419 | April | 2030 | 9760 |  |  | 6835 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 2925 | NA | NA | NA | 0 | 1
20250419 | April | 2130 | 9760 |  |  | 8335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1425 | NA | NA | NA | 0 | 1
20250419 | April | 2230 | 9760 |  |  | 9760 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250419 | April | 2330 | 8950 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 30 | 7806 |  |  | 7806 |  |  | -3406 | -3406 | -3406 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 130 | 7806 |  |  | 7806 |  |  | -3406 | -3406 | -3406 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 230 | 7806 |  |  | 7806 |  |  | -3406 | -3406 | -3406 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 330 | 7754 |  |  | 7754 |  |  | -3097 | -3097 | -3097 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 430 | 7754 |  |  | 7754 |  |  | -3097 | -3097 | -3097 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 530 | 7754 |  |  | 7754 |  |  | -3097 | -3097 | -3097 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 630 | 7754 |  |  | 6830 |  |  | -3097 | -3097 | -2170 | Critical Branch | Smoothing ramp | 0 | 924 | NA | NA | NA | 0 | 1
20250420 | April | 730 | 9250 |  |  | 5330 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 3920 | NA | NA | NA | 0 | 1
20250420 | April | 830 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 930 | 7080 |  |  | 3830 |  |  | -3081 | -3081 | 169 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 3419 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1030 | 7080 |  |  | 3830 |  |  | -3081 | -3081 | 169 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 3419 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1130 | 7080 |  |  | 3830 |  |  | -3081 | -3081 | 169 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 3419 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1230 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1330 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1430 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1530 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1630 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1730 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1830 | 7443 |  |  | 3830 |  |  | 3544 | 144 | 7013 | Minimum Margin | Validation phase | 3400 | 3613 | NA | NA | NA | 13882 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1930 | 7443 |  |  | 5330 |  |  | 3544 | 144 | 5497 | Minimum Margin | Smoothing ramp | 3400 | 2113 | NA | NA | NA | 10850 | 1
20250420 | April | 2030 | 7443 |  |  | 6830 |  |  | 3544 | 144 | 4008 | Minimum Margin | Smoothing ramp | 3400 | 613 | NA | NA | NA | 7872 | 1
20250420 | April | 2130 | 7098 |  |  | 7098 |  |  | -3130 | -3130 | -3130 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 2230 | 7098 |  |  | 7098 |  |  | -3130 | -3130 | -3130 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250420 | April | 2330 | 7098 |  |  | 7098 |  |  | -3130 | -3130 | -3130 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 30 | 7180 |  |  | 7180 |  |  | -5049 | -5049 | -5049 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 130 | 7180 |  |  | 7180 |  |  | -5049 | -5049 | -5049 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 230 | 7180 |  |  | 7180 |  |  | -5049 | -5049 | -5049 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 330 | 8033 |  |  | 8033 |  |  | -3409 | -3409 | -3409 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 430 | 8033 |  |  | 8033 |  |  | -3409 | -3409 | -3409 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 530 | 8033 |  |  | 8033 |  |  | -3409 | -3409 | -3409 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 630 | 8033 |  |  | 6830 |  |  | -3409 | -3409 | -2203 | Critical Branch | Smoothing ramp | 0 | 1203 | NA | NA | NA | 0 | 1
20250421 | April | 730 | 7233 |  |  | 5330 |  |  | -727 | -727 | 1193 | Critical Branch | Smoothing ramp | 0 | 1903 | NA | NA | NA | 3113 | 1
20250421 | April | 830 | 7233 |  |  | 3830 |  |  | -727 | -727 | 2676 | Critical Branch | Validation phase | 0 | 3403 | NA | NA | NA | 6079 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 930 | 7080 |  |  | 3830 |  |  | -3519 | -3519 | -269 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1030 | 7080 |  |  | 3830 |  |  | -3519 | -3519 | -269 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1130 | 7080 |  |  | 3830 |  |  | -3519 | -3519 | -269 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1230 | 7080 |  |  | 3830 |  |  | -2901 | -2901 | 349 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 3599 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1330 | 7080 |  |  | 3830 |  |  | -2901 | -2901 | 349 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 3599 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1430 | 7080 |  |  | 3830 |  |  | -2901 | -2901 | 349 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 3599 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1530 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1630 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1730 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 5420 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1830 | 7080 |  |  | 3830 |  |  | -4944 | -4944 | -1694 | TTC Selection - LTTC | Validation phase | 0 | 3250 | NA | NA | NA | 0 | 1 | SI: 3500; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1930 | 7080 |  |  | 5330 |  |  | -4944 | -4944 | -3203 | TTC Selection - LTTC | Smoothing ramp | 0 | 1750 | NA | NA | NA | 0 | 1
20250421 | April | 2030 | 7080 |  |  | 6830 |  |  | -4944 | -4944 | -4696 | TTC Selection - LTTC | Smoothing ramp | 0 | 250 | NA | NA | NA | 0 | 1
20250421 | April | 2130 | 7200 |  |  | 7200 |  |  | -3174 | -3174 | -3174 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 2230 | 7200 |  |  | 7200 |  |  | -3174 | -3174 | -3174 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250421 | April | 2330 | 7200 |  |  | 7200 |  |  | -3174 | -3174 | -3174 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250422 | April | 30 | 7180 |  |  | 7180 |  |  | -5112 | -5112 | -5112 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250422 | April | 130 | 7180 |  |  | 7180 |  |  | -5112 | -5112 | -5112 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250422 | April | 230 | 7180 |  |  | 7180 |  |  | -5112 | -5112 | -5112 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250422 | April | 330 | 9250 |  |  | 8680 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 570 | NA | NA | NA | 0 | 1
20250422 | April | 430 | 9250 |  |  | 8750 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250422 | April | 530 | 9250 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1219 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 630 | 9050 |  |  | 6531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2519 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6201; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered |  |  | 7010 | Foreseen violations on the border
20250422 | April | 730 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3629 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered |  |  | 7093 | Foreseen violations on the border
20250422 | April | 830 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3629 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered |  |  | 7093 | Foreseen violations on the border
20250422 | April | 930 | 9160 |  |  | 6167 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2993 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7093 | Foreseen violations on the border
20250422 | April | 1030 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2276 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1130 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2276 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1230 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3629 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250422 | April | 1330 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3629 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250422 | April | 1430 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 3629 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250422 | April | 1530 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2276 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1630 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2276 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1730 | 9160 |  |  | 6167 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2993 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7093 | Foreseen violations on the border
20250422 | April | 1830 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2633 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7253 | Foreseen violations on the border
20250422 | April | 1930 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2633 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7253 | Foreseen violations on the border
20250422 | April | 2030 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2633 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7253 | Foreseen violations on the border
20250422 | April | 2130 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2633 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7253 | Foreseen violations on the border
20250422 | April | 2230 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2633 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 7253 | Foreseen violations on the border
20250422 | April | 2330 | 8550 |  |  | 6197 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2353 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2 |  |  | 6610 | Foreseen violations on the border
20250423 | April | 30 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 130 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 230 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 330 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 430 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 530 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 630 | 8350 |  |  | 6912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 730 |  | 6005 | 627 |  | 4927 | 627 | -1759 | -1759 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1078 | 0 | 1078 | 1759 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 830 |  | 6005 | 627 |  | 4927 | 627 | -1759 | -1759 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1078 | 0 | 1078 | 1759 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 930 | 6990 |  |  | 5531 |  |  | -3579 | -3579 | -1102 | TTC Selection - LTTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1030 | 6990 |  |  | 5531 |  |  | -3579 | -3579 | -1102 | TTC Selection - LTTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1130 | 6990 |  |  | 5531 |  |  | -3579 | -3579 | -1102 | TTC Selection - LTTC | Validation phase | 0 | 1459 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1230 | 9160 |  |  | 6215 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2945 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7176; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1330 | 9160 |  |  | 6215 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2945 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7176; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1430 | 9160 |  |  | 6215 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2945 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2; SI: 7176; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1530 | 9160 |  |  | 7175 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1985 | NA | NA | NA | 0 | 1 | FR: 1600; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1630 | 9160 |  |  | 7175 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1985 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1730 | 9160 |  |  | 7175 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1985 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1830 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1930 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2030 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2130 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2230 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1585 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2330 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 30 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 130 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 230 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 330 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 430 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1438 | NA | NA | NA | 0 | 1 | FR: 2000; FR: Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 530 | 8550 |  |  | 6211 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 2339 | NA | NA | NA | 0 | 0
20250424 | April | 630 | 8350 |  |  | 4711 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 3639 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250424 | April | 730 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 679 | NA | NA | NA | 0 | 1 | [28 empty] | 2961 | Foreseen violations on the border
20250424 | April | 830 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 679 | NA | NA | NA | 0 | 1 | [28 empty] | 2961 | Foreseen violations on the border
20250424 | April | 930 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 679 | NA | NA | NA | 0 | 1 | [28 empty] | 2961 | Foreseen violations on the border
20250424 | April | 1030 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 679 | NA | NA | NA | 0 | 1 | [28 empty] | 2961 | Foreseen violations on the border
20250424 | April | 1130 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 679 | NA | NA | NA | 0 | 1 | [28 empty] | 2961 | Foreseen violations on the border
20250424 | April | 1230 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 679 | NA | NA | NA | 0 | 1 | [28 empty] | 2961 | Foreseen violations on the border
20250424 | April | 1330 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 696 | NA | NA | NA | 0 | 1 | [28 empty] | 2944 | Foreseen violations on the border
20250424 | April | 1430 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 696 | NA | NA | NA | 0 | 1 | [28 empty] | 2944 | Foreseen violations on the border
20250424 | April | 1530 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 696 | NA | NA | NA | 0 | 1 | [28 empty] | 2944 | Foreseen violations on the border
20250424 | April | 1630 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 696 | NA | NA | NA | 0 | 1 | [28 empty] | 2944 | Foreseen violations on the border
20250424 | April | 1730 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 696 | NA | NA | NA | 0 | 1 | [28 empty] | 2944 | Foreseen violations on the border
20250424 | April | 1830 | 4200 |  |  | 4199 |  |  | 6986 | 25 | 6962 | Minimum Margin | Validation phase | 6961 | 1 | NA | NA | NA | 13899 | 0
20250424 | April | 1930 | 4192 |  |  | 4192 |  |  | 6986 | 17 | 6969 | Minimum Margin | Minimum Margin | 6969 | 0 | NA | NA | NA | 13921 | 0
20250424 | April | 2030 | 4190 |  |  | 4189 |  |  | 6986 | 15 | 6972 | Minimum Margin | Validation phase | 6971 | 1 | NA | NA | NA | 13929 | 0
20250424 | April | 2130 | 6696 |  |  | 5689 |  |  | 2232 | 12 | 3222 | Minimum Margin | Smoothing ramp | 2220 | 1007 | NA | NA | NA | 6432 | 1
20250424 | April | 2230 | 6694 |  |  | 6694 |  |  | 2232 | 10 | 2222 | Minimum Margin | Minimum Margin | 2222 | 0 | NA | NA | NA | 4434 | 0
20250424 | April | 2330 | 6103 |  |  | 6103 |  |  | 2973 | 234 | 2739 | Minimum Margin | Minimum Margin | 2739 | 0 | NA | NA | NA | 5244 | 0
20250425 | April | 30 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 6500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 130 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 6500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 230 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 6500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 330 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 6500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 430 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 6500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 530 | 7330 |  |  | 6168 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1162 | NA | NA | NA | 0 | 1 | CH: 6500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 630 | 7130 |  |  | 4668 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 2462 | NA | NA | NA | 0 | 1 | CH: 6300; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 730 | 3168 |  |  | 3168 |  |  | 8204 | 8 | 8196 | Minimum Margin | Minimum Margin | 8196 | 0 | NA | NA | NA | 16384 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 830 | 3168 |  |  | 3168 |  |  | 8204 | 8 | 8196 | Minimum Margin | Minimum Margin | 8196 | 0 | NA | NA | NA | 16384 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 930 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1030 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1130 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1230 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1330 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1430 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1530 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1630 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | CH: 4500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1730 | 6960 |  |  | 4660 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Smoothing ramp | 0 | 2300 | NA | NA | NA | 0 | 1 | CH: 8300; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1830 | 9330 |  |  | 6160 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 3170 | NA | NA | NA | 0 | 1 | CH: 8500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1930 | 9330 |  |  | 7660 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1670 | NA | NA | NA | 0 | 1 | CH: 8500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2030 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 8500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2130 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 8500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2230 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 8500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2330 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 8500; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250426 | April | 30 | 7568 |  |  | 7552 |  |  | 2179 | 108 | 2087 | Minimum Margin | Validation phase | 2071 | 16 | NA | NA | NA | 4066 | 0
20250426 | April | 130 | 7568 |  |  | 7552 |  |  | 2179 | 108 | 2087 | Minimum Margin | Validation phase | 2071 | 16 | NA | NA | NA | 4066 | 0
20250426 | April | 230 | 7568 |  |  | 7552 |  |  | 2179 | 108 | 2087 | Minimum Margin | Validation phase | 2071 | 16 | NA | NA | NA | 4066 | 0
20250426 | April | 330 | 7590 |  |  | 7574 |  |  | 1525 | 130 | 1411 | Minimum Margin | Validation phase | 1395 | 16 | NA | NA | NA | 2692 | 0
20250426 | April | 430 | 7657 |  |  | 7633 |  |  | 1525 | 197 | 1352 | Minimum Margin | Validation phase | 1328 | 24 | NA | NA | NA | 2507 | 0
20250426 | April | 530 | 7704 |  |  | 7674 |  |  | 1525 | 244 | 1311 | Minimum Margin | Validation phase | 1281 | 30 | NA | NA | NA | 2378 | 0
20250426 | April | 630 | 7460 |  |  | 6330 |  |  | 1525 | 0 | 2655 | TTC Selection - LTTC | Validation phase | 1525 | 1130 | NA | NA | NA | 5310 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 730 | 10345 |  |  | 7830 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 2515 | NA | NA | NA | 0 | 1 | SI: 8682; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 830 | 10345 |  |  | 9017 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1328 | NA | NA | NA | 0 | 1 | SI: 8682; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 930 | 8175 |  |  | 8175 |  |  | 3371 | 0 | 3371 | TTC Selection - LTTC | TTC Selection - LTTC | 3371 | 0 | NA | NA | NA | 3371 | 0
20250426 | April | 1030 | 8309 |  |  | 7247 |  |  | 3371 | 134 | 4299 | Minimum Margin | Validation phase | 3237 | 1062 | NA | NA | NA | 8464 | 1 | SI: 6912; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 1130 | 8305 |  |  | 7245 |  |  | 3371 | 130 | 4301 | Minimum Margin | Validation phase | 3241 | 1060 | NA | NA | NA | 8472 | 1 | SI: 6910; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 1230 | 8175 |  |  | 8175 |  |  | -4237 | -4237 | -4237 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 1330 | 8175 |  |  | 8175 |  |  | -4237 | -4237 | -4237 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 1430 | 8175 |  |  | 8175 |  |  | -4237 | -4237 | -4237 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 1530 |  | 7307 | 710 |  | 7307 | 710 | -3181 | -3181 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3181 | 0
20250426 | April | 1630 |  | 7307 | 710 |  | 7307 | 710 | -3181 | -3181 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3181 | 0
20250426 | April | 1730 |  | 7307 | 710 |  | 7307 | 710 | -3181 | -3181 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 3181 | 0
20250426 | April | 1830 | 10345 |  |  | 9675 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 670 | NA | NA | NA | 0 | 1
20250426 | April | 1930 | 10345 |  |  | 10345 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 2030 | 10345 |  |  | 10345 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 2130 | 10345 |  |  | 10345 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 2230 | 10345 |  |  | 10345 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250426 | April | 2330 | 9530 |  |  | 9530 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250427 | April | 30 | 7460 |  |  | 9030 |  |  | -2558 | -2558 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2558 | 0
20250427 | April | 130 | 7460 |  |  | 9030 |  |  | -2558 | -2558 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2558 | 0
20250427 | April | 230 | 7460 |  |  | 9030 |  |  | -2558 | -2558 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2558 | 0
20250427 | April | 330 | 7460 |  |  | 9030 |  |  | -2962 | -2962 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2962 | 0
20250427 | April | 430 | 7460 |  |  | 9030 |  |  | -2962 | -2962 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2962 | 0
20250427 | April | 530 | 7460 |  |  | 9030 |  |  | -2962 | -2962 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2962 | 0
20250427 | April | 630 | 7460 |  |  | 9030 |  |  | -2962 | -2962 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1570 | NA | NA | NA | 2962 | 0
20250427 | April | 730 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 500 | NA | NA | NA | 0 | 0
20250427 | April | 830 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 500 | NA | NA | NA | 0 | 0
20250427 | April | 930 | 7360 |  |  | 8008 |  |  | -1965 | -1965 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -648 | NA | NA | NA | 1965 | 1 | SI: 7678; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250427 | April | 1030 | 7360 |  |  | 8008 |  |  | -1965 | -1965 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -648 | NA | NA | NA | 1965 | 1 | SI: 7678; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250427 | April | 1130 | 7360 |  |  | 8008 |  |  | -1965 | -1965 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -648 | NA | NA | NA | 1965 | 1 | SI: 7678; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250427 | April | 1230 | 7787 |  |  | 9030 |  |  | -1184 | -1184 | 0 | Critical Branch | Scheduled TTC | 0 | -1243 | NA | NA | NA | 1184 | 0
20250427 | April | 1330 | 7787 |  |  | 9030 |  |  | -1184 | -1184 | 0 | Critical Branch | Scheduled TTC | 0 | -1243 | NA | NA | NA | 1184 | 0
20250427 | April | 1430 | 7787 |  |  | 9030 |  |  | -1184 | -1184 | 0 | Critical Branch | Scheduled TTC | 0 | -1243 | NA | NA | NA | 1184 | 0
20250427 | April | 1530 | 7360 |  |  | 9030 |  |  | -3464 | -3464 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1670 | NA | NA | NA | 3464 | 0
20250427 | April | 1630 | 7360 |  |  | 9030 |  |  | -3464 | -3464 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1670 | NA | NA | NA | 3464 | 0
20250427 | April | 1730 | 7360 |  |  | 9030 |  |  | -3464 | -3464 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1670 | NA | NA | NA | 3464 | 0
20250427 | April | 1830 | 7360 |  |  | 9030 |  |  | -3499 | -3499 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1670 | NA | NA | NA | 3499 | 0
20250427 | April | 1930 | 7360 |  |  | 9030 |  |  | -3499 | -3499 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1670 | NA | NA | NA | 3499 | 0
20250427 | April | 2030 | 7360 |  |  | 9030 |  |  | -3499 | -3499 | 0 | TTC Selection - LTTC | Scheduled TTC | 0 | -1670 | NA | NA | NA | 3499 | 0
20250427 | April | 2130 | 7360 |  |  | 9030 |  |  | 2459 | 0 | 0 | TTC Selection - LTTC | Scheduled TTC | 2459 | -1670 | NA | NA | NA | 0 | 0
20250427 | April | 2230 | 7396 |  |  | 9030 |  |  | 2459 | 36 | 0 | Minimum Margin | Scheduled TTC | 2423 | -1634 | NA | NA | NA | -36 | 1 | AT: 435; AT: 170
20250427 | April | 2330 | 7591 |  |  | 9030 |  |  | 2459 | 231 | 0 | Minimum Margin | Scheduled TTC | 2228 | -1439 | NA | NA | NA | -231 | 1 | AT: 435; AT: 170
20250428 | April | 30 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170
20250428 | April | 130 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170
20250428 | April | 230 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 435; AT: 170
20250428 | April | 330 | 7592 |  |  | 7592 |  |  | 828 | 132 | 696 | Minimum Margin | Minimum Margin | 696 | 0 | NA | NA | NA | 1260 | 1 | AT: 435; AT: 170
20250428 | April | 430 | 7592 |  |  | 7592 |  |  | 828 | 132 | 696 | Minimum Margin | Minimum Margin | 696 | 0 | NA | NA | NA | 1260 | 1 | AT: 435; AT: 170
20250428 | April | 530 | 7592 |  |  | 7592 |  |  | 828 | 132 | 696 | Minimum Margin | Minimum Margin | 696 | 0 | NA | NA | NA | 1260 | 1 | AT: 450; AT: 155
20250428 | April | 630 | 7497 |  |  | 7497 |  |  | 856 | 237 | 619 | Minimum Margin | Minimum Margin | 619 | 0 | NA | NA | NA | 1001 | 1 | AT: 450; AT: 155
20250428 | April | 730 | 6286 |  |  | 6286 |  |  | 2138 | 111 | 2027 | Minimum Margin | Minimum Margin | 2027 | 0 | NA | NA | NA | 3943 | 1 | AT: 450; AT: 155
20250428 | April | 830 | 6348 |  |  | 6348 |  |  | 2138 | 173 | 1965 | Minimum Margin | Minimum Margin | 1965 | 0 | NA | NA | NA | 3757 | 1 | AT: 450; AT: 155
20250428 | April | 930 | 6370 |  |  | 6370 |  |  | 2046 | 195 | 1851 | Minimum Margin | Minimum Margin | 1851 | 0 | NA | NA | NA | 3507 | 1 | AT: 450; AT: 155
20250428 | April | 1030 | 6363 |  |  | 6363 |  |  | 2046 | 188 | 1858 | Minimum Margin | Minimum Margin | 1858 | 0 | NA | NA | NA | 3528 | 1 | AT: 450; AT: 155
20250428 | April | 1130 | 6351 |  |  | 6351 |  |  | 2046 | 176 | 1870 | Minimum Margin | Minimum Margin | 1870 | 0 | NA | NA | NA | 3564 | 1 | AT: 450; AT: 155
20250428 | April | 1230 | 6611 |  |  | 6611 |  |  | -1000 | -1000 | -1000 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250428 | April | 1330 | 6611 |  |  | 6611 |  |  | -1000 | -1000 | -1000 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250428 | April | 1430 | 6611 |  |  | 6611 |  |  | -1000 | -1000 | -1000 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250428 | April | 1530 | 6355 |  |  | 6355 |  |  | 2258 | 180 | 2078 | Minimum Margin | Minimum Margin | 2078 | 0 | NA | NA | NA | 3976 | 1 | AT: 450; AT: 155
20250428 | April | 1630 | 6321 |  |  | 6321 |  |  | 2258 | 146 | 2112 | Minimum Margin | Minimum Margin | 2112 | 0 | NA | NA | NA | 4078 | 1 | AT: 450; AT: 155
20250428 | April | 1730 | 8230 |  |  | 7821 |  |  | 2279 | 255 | 2429 | Minimum Margin | Smoothing ramp | 2024 | 409 | NA | NA | NA | 4603 | 1 | AT: 450; AT: 155
20250428 | April | 1830 | 10345 |  |  | 9321 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1024 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250428 | April | 1930 | 10345 |  |  | 9845 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250428 | April | 2030 | 10345 |  |  | 9845 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 450; AT: 155
20250428 | April | 2130 | 8345 |  |  | 8345 |  |  | 1813 | 170 | 1643 | Minimum Margin | Minimum Margin | 1643 | 0 | NA | NA | NA | 3116 | 1 | AT: 435; AT: 170
20250428 | April | 2230 | 8345 |  |  | 8345 |  |  | 1813 | 170 | 1643 | Minimum Margin | Minimum Margin | 1643 | 0 | NA | NA | NA | 3116 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250428 | April | 2330 | 7520 |  |  | 7520 |  |  | 2148 | 160 | 1988 | Minimum Margin | Minimum Margin | 1988 | 0 | NA | NA | NA | 3816 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 30 | 7534 |  |  | 7534 |  |  | 174 | 154 | 20 | Minimum Margin | Minimum Margin | 20 | 0 | NA | NA | NA | -114 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 130 | 7534 |  |  | 7534 |  |  | 174 | 154 | 20 | Minimum Margin | Minimum Margin | 20 | 0 | NA | NA | NA | -114 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 230 | 7534 |  |  | 7534 |  |  | 174 | 154 | 20 | Minimum Margin | Minimum Margin | 20 | 0 | NA | NA | NA | -114 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 330 | 9450 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 430 | 9450 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 530 | 9450 |  |  | 8130 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1320 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 630 | 9250 |  |  | 6630 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2620 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 730 | 8586 |  |  | 7806 |  |  | 1121 | 451 | 1450 | Minimum Margin | Validation phase | 670 | 780 | NA | NA | NA | 2449 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 830 | 8586 |  |  | 7806 |  |  | 1121 | 451 | 1450 | Minimum Margin | Validation phase | 670 | 780 | NA | NA | NA | 2449 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 930 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2825 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1030 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2825 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1130 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2825 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1230 | 9136 |  |  | 6335 |  |  | -1759 | -1759 | 1042 | Critical Branch | Validation phase | 0 | 2801 | NA | NA | NA | 3843 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1330 | 9136 |  |  | 6335 |  |  | -1759 | -1759 | 1042 | Critical Branch | Validation phase | 0 | 2801 | NA | NA | NA | 3843 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1430 | 9136 |  |  | 6335 |  |  | -1759 | -1759 | 1042 | Critical Branch | Validation phase | 0 | 2801 | NA | NA | NA | 3843 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1530 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1630 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1730 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1830 | 7348 |  |  | 7348 |  |  | 3663 | 158 | 3505 | Minimum Margin | Minimum Margin | 3505 | 0 | NA | NA | NA | 6852 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 1930 | 7348 |  |  | 7348 |  |  | 3663 | 158 | 3505 | Minimum Margin | Minimum Margin | 3505 | 0 | NA | NA | NA | 6852 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 2030 | 7348 |  |  | 7348 |  |  | 3663 | 158 | 3505 | Minimum Margin | Minimum Margin | 3505 | 0 | NA | NA | NA | 6852 | 1 | AT: 450; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250429 | April | 2130 | 7360 |  |  | 7360 |  |  | 2976 | 170 | 2806 | Minimum Margin | Minimum Margin | 2806 | 0 | NA | NA | NA | 5442 | 1 | AT: 435; AT: Reduction because NTC over thermal limit on border; AT: 170; AT: Reduction because NTC over thermal limit on border
20250429 | April | 2230 | 7360 |  |  | 7360 |  |  | 2976 | 170 | 2806 | Minimum Margin | Minimum Margin | 2806 | 0 | NA | NA | NA | 5442 | 0
20250429 | April | 2330 | 6539 |  |  | 6539 |  |  | 3287 | 159 | 3128 | Minimum Margin | Minimum Margin | 3128 | 0 | NA | NA | NA | 6097 | 0
20250430 | April | 30 | 8550 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 130 | 8550 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 230 | 8550 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 330 | 8550 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 430 | 8550 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 530 | 8550 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 630 | 8350 |  |  | 8350 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 730 | 9160 |  |  | 7807 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1353 | NA | NA | NA | 0 | 0
20250430 | April | 830 | 9160 |  |  | 7807 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1353 | NA | NA | NA | 0 | 0
20250430 | April | 930 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2825 | NA | NA | NA | 0 | 0
20250430 | April | 1030 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2825 | NA | NA | NA | 0 | 0
20250430 | April | 1130 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2825 | NA | NA | NA | 0 | 0
20250430 | April | 1230 | 9160 |  |  | 7511 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1649 | NA | NA | NA | 0 | 0
20250430 | April | 1330 | 9160 |  |  | 7511 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1649 | NA | NA | NA | 0 | 0
20250430 | April | 1430 | 9160 |  |  | 7511 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1649 | NA | NA | NA | 0 | 0
20250430 | April | 1530 | 9160 |  |  | 9011 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 149 | NA | NA | NA | 0 | 1
20250430 | April | 1630 | 9160 |  |  | 9160 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250430 | April | 1730 | 10060 |  |  | 8758 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1302 | NA | NA | NA | 0 | 0
20250430 | April | 1830 | 10260 |  |  | 9500 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 760 | NA | NA | NA | 0 | 1
20250430 | April | 1930 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2260 | NA | NA | NA | 0 | 1 | [28 empty] | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2030 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2260 | NA | NA | NA | 0 | 1 | [28 empty] | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2130 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2260 | NA | NA | NA | 0 | 1 | [28 empty] | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2230 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 2260 | NA | NA | NA | 0 | 1 | AT: 332; AT: 160; FR: 2843; FR: Process fail during TSO validation phase |  |  | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2330 | 9450 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 1450 | NA | NA | NA | 0 | 1 | AT: 332; AT: 160; FR: 2843; FR: Process fail during TSO validation phase |  |  | 7670 | Allocation Constraint value not properly processed by Coreso
20250501 | May | 30 |  | 6209 | 559 |  | 6149 | 559 | 2413 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2297 | NA | 60 | 0 | 60 | -116 | 1 | AT: 332; AT: 160; FR: 2843; FR: Process fail during TSO validation phase
20250501 | May | 130 |  | 6209 | 559 |  | 6149 | 559 | 2413 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2297 | NA | 60 | 0 | 60 | -116 | 1 | AT: 309; AT: 160; FR: 2638; FR: Process fail during TSO validation phase
20250501 | May | 230 |  | 6209 | 559 |  | 6149 | 559 | 2413 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2297 | NA | 60 | 0 | 60 | -116 | 1 | AT: 309; AT: 160; FR: 2638; FR: Process fail during TSO validation phase
20250501 | May | 330 |  | 5803 | 395 |  | 5744 | 395 | 2502 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2386 | NA | 59 | 0 | 59 | -116 | 1 | AT: 309; AT: 160; FR: 2638; FR: Process fail during TSO validation phase
20250501 | May | 430 |  | 5803 | 395 |  | 5744 | 395 | 2502 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2386 | NA | 59 | 0 | 59 | -116 | 1 | AT: 306; AT: 160; FR: 2610; FR: Process fail during TSO validation phase
20250501 | May | 530 |  | 5803 | 395 |  | 5744 | 395 | 2502 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2386 | NA | 59 | 0 | 59 | -116 | 1 | AT: 341; AT: 160
20250501 | May | 630 |  | 5603 | 395 |  | 5542 | 395 | 2557 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2441 | NA | 61 | 0 | 61 | -116 | 1 | AT: 344; AT: 160
20250501 | May | 730 | 6638 |  |  | 6625 |  |  | 3526 | 126 | 3413 | Minimum Margin | Validation phase | 3400 | 13 | NA | NA | NA | 6700 | 1 | AT: 382; AT: 160
20250501 | May | 830 | 6683 |  |  | 6666 |  |  | 3526 | 171 | 3372 | Minimum Margin | Validation phase | 3355 | 17 | NA | NA | NA | 6573 | 1 | AT: 382; AT: 160
20250501 | May | 930 | 7373 |  |  | 7372 |  |  | -3046 | -3046 | -3045 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 382; AT: 160
20250501 | May | 1030 | 7373 |  |  | 7372 |  |  | -3046 | -3046 | -3045 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 305; AT: 160
20250501 | May | 1130 | 7373 |  |  | 7372 |  |  | -3046 | -3046 | -3045 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 305; AT: 160
20250501 | May | 1230 | 5980 |  |  | 5980 |  |  | -1806 | -1806 | -1806 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 305; AT: 160
20250501 | May | 1330 | 5980 |  |  | 5980 |  |  | -1806 | -1806 | -1806 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 388; AT: 160
20250501 | May | 1430 | 5980 |  |  | 5980 |  |  | -1806 | -1806 | -1806 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 400; AT: 160
20250501 | May | 1530 | 7696 |  |  | 7480 |  |  | -2511 | -2511 | -2295 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 216 | NA | NA | NA | 0 | 1 | AT: 394; AT: 160
20250501 | May | 1630 | 7696 |  |  | 7576 |  |  | -2511 | -2511 | -2391 | Critical Branch | Validation phase | 0 | 120 | NA | NA | NA | 0 | 1 | AT: 297; AT: 114; FR: 2591; FR: Process fail during TSO validation phase
20250501 | May | 1730 | 7696 |  |  | 7529 |  |  | -2511 | -2511 | -2344 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 167 | NA | NA | NA | 0 | 1 | AT: 297; AT: 115; FR: 2591; FR: Process fail during TSO validation phase
20250501 | May | 1830 |  | 5376 | 638 |  | 5319 | 637 | 3424 | 107 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3317 | NA | 57 | 1 | 58 | -107 | 1 | AT: 297; AT: 116; FR: 2591; FR: Process fail during TSO validation phase
20250501 | May | 1930 |  | 5398 | 640 |  | 5329 | 640 | 3424 | 128 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3296 | NA | 69 | 0 | 69 | -128 | 1 | AT: 401; AT: 160; FR: 3618; FR: Process fail during TSO validation phase
20250501 | May | 2030 |  | 5449 | 646 |  | 5353 | 645 | 3424 | 180 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3244 | NA | 96 | 1 | 97 | -180 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3618; FR: Process fail during TSO validation phase
20250501 | May | 2130 |  | 7678 | 717 |  | 7303 | 717 | 1422 | 51 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1371 | NA | 375 | 0 | 375 | -51 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; FR: 3618; FR: Process fail during TSO validation phase
20250501 | May | 2230 |  | 7783 | 726 |  | 7694 | 726 | 1422 | 156 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1266 | NA | 89 | 0 | 89 | -156 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250501 | May | 2330 |  | 7758 | 724 |  | 7683 | 724 | 1422 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1290 | NA | 75 | 0 | 75 | -132 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250502 | May | 30 | 8316 |  |  | 8308 |  |  | -3710 | -3710 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250502 | May | 130 | 8316 |  |  | 8308 |  |  | -3710 | -3710 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 415; AT: 151
20250502 | May | 230 | 8316 |  |  | 8308 |  |  | -3710 | -3710 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 8 | NA | NA | NA | 0 | 1 | AT: 415; AT: 151
20250502 | May | 330 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1141 | 1 | AT: 415; AT: 151
20250502 | May | 430 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1141 | 1 | AT: 415; AT: 151
20250502 | May | 530 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1141 | 1 | AT: 361; AT: 135
20250502 | May | 630 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1141 | 1 | AT: 361; AT: 135
20250502 | May | 730 |  | 6836 | 766 |  | 6835 | 766 | -941 | -941 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 941 | 1 | AT: 329; AT: 140
20250502 | May | 830 |  | 6836 | 766 |  | 6835 | 766 | -941 | -941 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 941 | 1 | AT: 329; AT: 140
20250502 | May | 930 | 6580 |  |  | 6579 |  |  | -2596 | -2596 | -2595 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250502 | May | 1030 | 6580 |  |  | 6579 |  |  | -2596 | -2596 | -2595 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250502 | May | 1130 | 6580 |  |  | 6579 |  |  | -2596 | -2596 | -2595 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250502 | May | 1230 | 6580 |  |  | 6579 |  |  | -2616 | -2616 | -2615 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250502 | May | 1330 | 6580 |  |  | 6579 |  |  | -2616 | -2616 | -2615 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 392; AT: 140
20250502 | May | 1430 | 6580 |  |  | 6579 |  |  | -2616 | -2616 | -2615 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 412; AT: 140
20250502 | May | 1530 | 8475 |  |  | 8079 |  |  | -2787 | -2787 | -2394 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 396 | NA | NA | NA | 0 | 1 | AT: 412; AT: 140
20250502 | May | 1630 | 8475 |  |  | 8474 |  |  | -2787 | -2787 | -2786 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 234; AT: 132; FR: 3609; FR: Process fail during TSO validation phase
20250502 | May | 1730 | 8475 |  |  | 8474 |  |  | -2787 | -2787 | -2786 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 234; AT: 132; FR: 3609; FR: Process fail during TSO validation phase
20250502 | May | 1830 |  | 7379 | 769 |  | 7332 | 769 | 2054 | 88 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1966 | NA | 47 | 0 | 47 | -88 | 1 | AT: 234; AT: 131; FR: 3609; FR: Process fail during TSO validation phase
20250502 | May | 1930 |  | 7373 | 768 |  | 7330 | 768 | 2054 | 82 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1972 | NA | 43 | 0 | 43 | -82 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border
20250502 | May | 2030 |  | 7371 | 768 |  | 7329 | 767 | 2054 | 80 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1974 | NA | 42 | 1 | 43 | -80 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border
20250502 | May | 2130 |  | 8818 | 766 |  | 8788 | 766 | -3741 | -3741 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 30 | 0 | 30 | 3741 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250502 | May | 2230 |  | 8818 | 766 |  | 8788 | 766 | -3741 | -3741 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 30 | 0 | 30 | 3741 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250502 | May | 2330 |  | 8238 | 791 |  | 8207 | 791 | -3097 | -3097 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 31 | 0 | 31 | 3097 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250503 | May | 30 |  | 8329 | 809 |  | 8294 | 809 | -2715 | -2715 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 35 | 0 | 35 | 2715 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250503 | May | 130 |  | 8329 | 809 |  | 8294 | 809 | -2715 | -2715 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 35 | 0 | 35 | 2715 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250503 | May | 230 |  | 8329 | 809 |  | 8294 | 809 | -2715 | -2715 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 35 | 0 | 35 | 2715 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250503 | May | 330 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 2647 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250503 | May | 430 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 2647 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250503 | May | 530 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 2647 | 1 | AT: 385; AT: 139
20250503 | May | 630 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 2647 | 1 | AT: 385; AT: 139
20250503 | May | 730 |  | 7353 | 660 |  | 7352 | 660 | -1475 | -1475 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1475 | 1 | AT: 339; AT: 140
20250503 | May | 830 |  | 7353 | 660 |  | 7352 | 660 | -1475 | -1475 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1475 | 1 | AT: 339; AT: 140
20250503 | May | 930 | 6806 |  |  | 6806 |  |  | -2916 | -2916 | -2915 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 339; AT: 140
20250503 | May | 1030 | 6806 |  |  | 6806 |  |  | -2916 | -2916 | -2915 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250503 | May | 1130 | 6806 |  |  | 6806 |  |  | -2916 | -2916 | -2915 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250503 | May | 1230 | 6580 |  |  | 6579 |  |  | -2607 | -2607 | -2606 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250503 | May | 1330 | 6580 |  |  | 6579 |  |  | -2607 | -2607 | -2606 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250503 | May | 1430 | 6580 |  |  | 6579 |  |  | -2607 | -2607 | -2606 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 329; AT: 140
20250503 | May | 1530 |  | 6155 | 321 |  | 6154 | 321 | -2115 | -2115 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2115 | 1 | AT: 329; AT: 140
20250503 | May | 1630 |  | 6155 | 321 |  | 6154 | 321 | -2115 | -2115 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2115 | 1 | AT: 397; AT: 140
20250503 | May | 1730 |  | 6155 | 321 |  | 6154 | 321 | -2115 | -2115 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2115 | 1 | AT: 397; AT: 140
20250503 | May | 1830 |  | 7591 | 609 |  | 7591 | 609 | -1216 | -1216 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1216 | 1 | AT: 397; AT: 140
20250503 | May | 1930 |  | 7591 | 609 |  | 7591 | 609 | -1216 | -1216 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1216 | 1 | AT: 404; AT: 140
20250503 | May | 2030 |  | 7591 | 609 |  | 7591 | 609 | -1216 | -1216 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1216 | 1 | AT: 404; AT: 140
20250503 | May | 2130 | 8286 |  |  | 8285 |  |  | -1836 | -1836 | -1835 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 393; AT: 160
20250503 | May | 2230 | 8286 |  |  | 8285 |  |  | -1836 | -1836 | -1835 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250503 | May | 2330 | 7686 |  |  | 7686 |  |  | -1217 | -1217 | -1217 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250504 | May | 30 |  | 7902 | 730 |  | 7888 | 730 | -1420 | -1420 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 1420 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250504 | May | 130 |  | 7902 | 730 |  | 7888 | 730 | -1420 | -1420 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 1420 | 1 | AT: 209; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 230 |  | 7902 | 730 |  | 7888 | 730 | -1420 | -1420 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 1420 | 1 | AT: 209; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 330 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 1117 | 1 | AT: 209; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 430 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 1117 | 1 | AT: 209; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 530 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 1117 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250504 | May | 630 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 20 | 20 | 1117 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250504 | May | 730 |  | 8168 | 787 |  | 8141 | 787 | -2489 | -2489 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 27 | 0 | 27 | 2489 | 1 | AT: 397; AT: 160
20250504 | May | 830 |  | 8168 | 787 |  | 8141 | 787 | -2489 | -2489 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 27 | 0 | 27 | 2489 | 1 | AT: 397; AT: 160
20250504 | May | 930 | 7770 |  |  | 7770 |  |  | -3922 | -3922 | -3922 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 397; AT: 160
20250504 | May | 1030 | 7770 |  |  | 7770 |  |  | -3922 | -3922 | -3922 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 160
20250504 | May | 1130 | 7770 |  |  | 7770 |  |  | -3922 | -3922 | -3922 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 160
20250504 | May | 1230 | 7218 |  |  | 7218 |  |  | -3321 | -3321 | -3321 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 160
20250504 | May | 1330 | 7218 |  |  | 7218 |  |  | -3321 | -3321 | -3321 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 212; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 1430 | 7218 |  |  | 7218 |  |  | -3321 | -3321 | -3321 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 212; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 1530 |  | 7823 | 959 |  | 7823 | 940 | -4266 | -4266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 19 | 19 | 4266 | 1 | AT: 212; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250504 | May | 1630 |  | 7823 | 959 |  | 7823 | 940 | -4266 | -4266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 19 | 19 | 4266 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250504 | May | 1730 |  | 7823 | 959 |  | 7823 | 940 | -4266 | -4266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 19 | 19 | 4266 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250504 | May | 1830 |  | 7881 | 718 |  | 7868 | 718 | -1611 | -1611 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 13 | 0 | 13 | 1611 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250504 | May | 1930 |  | 7881 | 718 |  | 7868 | 718 | -1611 | -1611 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 13 | 0 | 13 | 1611 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250504 | May | 2030 |  | 7881 | 718 |  | 7868 | 718 | -1611 | -1611 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 13 | 0 | 13 | 1611 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250504 | May | 2130 |  | 7700 | 718 |  | 7696 | 718 | -776 | -776 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 4 | 0 | 4 | 776 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250504 | May | 2230 |  | 7700 | 718 |  | 7696 | 718 | -776 | -776 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 4 | 0 | 4 | 776 | 1 | AT: 185; AT: 159; FR: 3447; FR: Process fail during TSO validation phase
20250504 | May | 2330 |  | 7700 | 718 |  | 7696 | 718 | -776 | -776 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 4 | 0 | 4 | 776 | 1 | AT: 185; AT: 159; FR: 3447; FR: Process fail during TSO validation phase
20250505 | May | 30 |  | 6915 | 863 |  | 6888 | 862 | 76 | 50 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 26 | NA | 27 | 1 | 28 | -50 | 1 | AT: 185; AT: 159; FR: 3447; FR: Process fail during TSO validation phase
20250505 | May | 130 |  | 6915 | 863 |  | 6888 | 862 | 76 | 50 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 26 | NA | 27 | 1 | 28 | -50 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250505 | May | 230 |  | 6915 | 863 |  | 6888 | 862 | 76 | 50 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 26 | NA | 27 | 1 | 28 | -50 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250505 | May | 330 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 18 | 18 | 1383 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250505 | May | 430 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 18 | 18 | 1383 | 1 | AT: 190; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250505 | May | 530 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 18 | 18 | 1383 | 1 | AT: 263; AT: 89; FR: 2904; FR: Process fail during TSO validation phase
20250505 | May | 630 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 18 | 18 | 1383 | 1 | AT: 260; AT: 86; FR: 2784; FR: Process fail during TSO validation phase
20250505 | May | 730 |  | 6474 | 116 |  | 6431 | 115 | 4192 | 87 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4105 | NA | 43 | 1 | 44 | -87 | 1 | AT: 299; AT: 140
20250505 | May | 830 |  | 5574 | 116 |  | 5525 | 115 | 4438 | 87 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4351 | NA | 49 | 1 | 50 | -87 | 1 | AT: 308; AT: 140
20250505 | May | 930 | 5688 |  |  | 5687 |  |  | 3916 | 8 | 3908 | Minimum Margin | TTC Validation phase - bilateral reduction | 3908 | 1 | NA | NA | NA | 7808 | 1 | AT: 308; AT: 140
20250505 | May | 1030 | 5827 |  |  | 5814 |  |  | 3916 | 147 | 3782 | Minimum Margin | Validation phase | 3769 | 13 | NA | NA | NA | 7417 | 1 | AT: 299; AT: 69; FR: 2709; FR: Process fail during TSO validation phase
20250505 | May | 1130 | 5827 |  |  | 5814 |  |  | 3916 | 147 | 3782 | Minimum Margin | Validation phase | 3769 | 13 | NA | NA | NA | 7417 | 1 | AT: 299; AT: 69; FR: 2709; FR: Process fail during TSO validation phase
20250505 | May | 1230 |  | 5040 | 444 |  | 4979 | 443 | 3204 | 101 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3103 | NA | 61 | 1 | 62 | -101 | 1 | AT: 299; AT: 69; FR: 2709; FR: Process fail during TSO validation phase
20250505 | May | 1330 |  | 5024 | 442 |  | 4973 | 442 | 3204 | 85 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3119 | NA | 51 | 0 | 51 | -85 | 1 | AT: 306; AT: 140
20250505 | May | 1430 |  | 5047 | 445 |  | 4982 | 444 | 3204 | 108 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3096 | NA | 65 | 1 | 66 | -108 | 1 | AT: 311; AT: 140
20250505 | May | 1530 | 5800 |  |  | 5790 |  |  | 4117 | 120 | 4007 | Minimum Margin | Validation phase | 3997 | 10 | NA | NA | NA | 7894 | 1 | AT: 306; AT: 140
20250505 | May | 1630 | 5890 |  |  | 5870 |  |  | 4117 | 210 | 3927 | Minimum Margin | Validation phase | 3907 | 20 | NA | NA | NA | 7644 | 1 | AT: 161; AT: 114
20250505 | May | 1730 | 5796 |  |  | 5786 |  |  | 4117 | 116 | 4011 | Minimum Margin | Validation phase | 4001 | 10 | NA | NA | NA | 7906 | 1 | AT: 161; AT: 114
20250505 | May | 1830 |  | 5650 | 685 |  | 5650 | 685 | -2694 | -2694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2694 | 1 | AT: 161; AT: 114
20250505 | May | 1930 |  | 5650 | 685 |  | 5650 | 685 | -2694 | -2694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2694 | 1 | AT: 341; AT: 140
20250505 | May | 2030 |  | 5650 | 685 |  | 5650 | 685 | -2694 | -2694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2694 | 1 | AT: 341; AT: 140
20250505 | May | 2130 |  | 5941 | 540 |  | 5940 | 540 | -1215 | -1215 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1215 | 1 | AT: 326; AT: 160
20250505 | May | 2230 |  | 5941 | 540 |  | 5940 | 540 | -1215 | -1215 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1215 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250505 | May | 2330 |  | 5381 | 565 |  | 5381 | 565 | -586 | -586 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 586 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250506 | May | 30 |  | 7821 | 870 |  | 7748 | 870 | -2810 | -2810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 73 | 0 | 73 | 2810 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250506 | May | 130 |  | 7821 | 870 |  | 7748 | 870 | -2810 | -2810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 73 | 0 | 73 | 2810 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250506 | May | 230 |  | 7821 | 870 |  | 7748 | 870 | -2810 | -2810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 73 | 0 | 73 | 2810 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250506 | May | 330 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 57 | 0 | 57 | 2451 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250506 | May | 430 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 57 | 0 | 57 | 2451 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250506 | May | 530 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 57 | 0 | 57 | 2451 | 1 | AT: 378; AT: 140
20250506 | May | 630 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 57 | 0 | 57 | 2451 | 1 | AT: 378; AT: 140
20250506 | May | 730 | 7054 |  |  | 7053 |  |  | -998 | -998 | -997 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 310; AT: 140
20250506 | May | 830 | 7054 |  |  | 7053 |  |  | -998 | -998 | -997 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 311; AT: 140
20250506 | May | 930 | 5876 |  |  | 5867 |  |  | 3798 | 196 | 3611 | Minimum Margin | Validation phase | 3602 | 9 | NA | NA | NA | 7026 | 1 | AT: 308; AT: 140
20250506 | May | 1030 | 5882 |  |  | 5870 |  |  | 3798 | 202 | 3608 | Minimum Margin | Validation phase | 3596 | 12 | NA | NA | NA | 7014 | 1 | AT: 395; AT: 140
20250506 | May | 1130 | 5835 |  |  | 5828 |  |  | 3798 | 155 | 3650 | Minimum Margin | Validation phase | 3643 | 7 | NA | NA | NA | 7145 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250506 | May | 1230 | 8034 |  |  | 7328 |  |  | 1295 | 122 | 1851 | Minimum Margin | TTC Validation phase - bilateral reduction | 1173 | 706 | NA | NA | NA | 3580 | 1 | AT: 393; AT: 140
20250506 | May | 1330 | 8034 |  |  | 8015 |  |  | 1295 | 122 | 1184 | Minimum Margin | Validation phase | 1173 | 19 | NA | NA | NA | 2246 | 1 | AT: 306; AT: 140
20250506 | May | 1430 | 8034 |  |  | 7288 |  |  | 1295 | 122 | 1890 | Minimum Margin | TTC Validation phase - bilateral reduction | 1173 | 746 | NA | NA | NA | 3658 | 1 | AT: 308; AT: 140
20250506 | May | 1530 | 5797 |  |  | 5788 |  |  | 3647 | 117 | 3539 | Minimum Margin | Validation phase | 3530 | 9 | NA | NA | NA | 6961 | 1 | AT: 310; AT: 140
20250506 | May | 1630 | 5839 |  |  | 5826 |  |  | 3647 | 159 | 3501 | Minimum Margin | Validation phase | 3488 | 13 | NA | NA | NA | 6843 | 1 | AT: 372; AT: 140
20250506 | May | 1730 | 5870 |  |  | 5854 |  |  | 3647 | 190 | 3473 | Minimum Margin | Validation phase | 3457 | 16 | NA | NA | NA | 6756 | 1 | AT: 368; AT: 140
20250506 | May | 1830 |  | 6432 | 594 |  | 6431 | 594 | 1662 | 154 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1508 | NA | 1 | 0 | 1 | -154 | 1 | AT: 371; AT: 140
20250506 | May | 1930 |  | 6370 | 588 |  | 6369 | 588 | 1662 | 92 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1570 | NA | 1 | 0 | 1 | -92 | 1 | AT: 411; AT: 140
20250506 | May | 2030 |  | 6414 | 592 |  | 6414 | 592 | 1662 | 136 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1526 | NA | 0 | 0 | 0 | -136 | 1 | AT: 411; AT: 140
20250506 | May | 2130 |  | 7066 | 642 |  | 7036 | 639 | -2017 | -2017 | 0 | Critical Branch | Validation phase | 0 | NA | 30 | 3 | 33 | 2017 | 1 | AT: 399; AT: 160
20250506 | May | 2230 |  | 7066 | 642 |  | 7036 | 639 | -2017 | -2017 | 0 | Critical Branch | Validation phase | 0 | NA | 30 | 3 | 33 | 2017 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250506 | May | 2330 |  | 6490 | 667 |  | 6475 | 666 | -1358 | -1358 | 0 | Critical Branch | Validation phase | 0 | NA | 15 | 1 | 16 | 1358 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250507 | May | 30 |  | 7277 | 812 |  | 7240 | 812 | -2000 | -2000 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 37 | 0 | 37 | 2000 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250507 | May | 130 |  | 7277 | 812 |  | 7240 | 812 | -2000 | -2000 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 37 | 0 | 37 | 2000 | 1 | AT: 404; AT: 160
20250507 | May | 230 |  | 7277 | 812 |  | 7240 | 812 | -2000 | -2000 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 37 | 0 | 37 | 2000 | 1 | AT: 404; AT: 160
20250507 | May | 330 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 3900 | 1 | AT: 404; AT: 160
20250507 | May | 430 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 3900 | 1 | AT: 404; AT: 160
20250507 | May | 530 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 3900 | 1 | AT: 404; AT: 138
20250507 | May | 630 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 3900 | 1 | AT: 347; AT: 118
20250507 | May | 730 |  | 6957 | 705 |  | 6956 | 705 | -1703 | -1703 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1703 | 1 | AT: 365; AT: 120
20250507 | May | 830 |  | 6897 | 705 |  | 6896 | 705 | -1641 | -1641 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1641 | 1 | AT: 365; AT: 120
20250507 | May | 930 | 7790 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1540 | NA | NA | NA | 0 | 1 | AT: 337; AT: 120
20250507 | May | 1030 | 7790 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1540 | NA | NA | NA | 0 | 1 | AT: 262; AT: 120
20250507 | May | 1130 | 7790 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1540 | NA | NA | NA | 0 | 1 | AT: 262; AT: 120
20250507 | May | 1230 | 5746 |  |  | 5737 |  |  | 2761 | 126 | 2644 | Minimum Margin | Validation phase | 2635 | 9 | NA | NA | NA | 5162 | 1 | AT: 262; AT: 120
20250507 | May | 1330 | 5746 |  |  | 5737 |  |  | 2761 | 126 | 2644 | Minimum Margin | Validation phase | 2635 | 9 | NA | NA | NA | 5162 | 1 | AT: 263; AT: 120; FR: 2699; FR: Process fail during TSO validation phase
20250507 | May | 1430 | 5746 |  |  | 5737 |  |  | 2761 | 126 | 2644 | Minimum Margin | Validation phase | 2635 | 9 | NA | NA | NA | 5162 | 1 | AT: 306; AT: 140; FR: 2708; FR: Process fail during TSO validation phase
20250507 | May | 1530 |  | 5326 | 337 |  | 5258 | 337 | 2382 | 119 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2263 | NA | 68 | 0 | 68 | -119 | 1 | AT: 306; AT: 140; FR: 2708; FR: Process fail during TSO validation phase
20250507 | May | 1630 |  | 5386 | 337 |  | 5317 | 337 | 2355 | 119 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2236 | NA | 69 | 0 | 69 | -119 | 1 | AT: 359; AT: 140
20250507 | May | 1730 |  | 5386 | 337 |  | 5317 | 337 | 2355 | 119 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2236 | NA | 69 | 0 | 69 | -119 | 1 | AT: 350; AT: 140
20250507 | May | 1830 |  | 6237 | 587 |  | 6236 | 587 | 2602 | 396 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2206 | NA | 1 | 0 | 1 | -396 | 1 | AT: 339; AT: 140
20250507 | May | 1930 |  | 6087 | 573 |  | 6086 | 573 | 2602 | 246 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2356 | NA | 1 | 0 | 1 | -246 | 1 | AT: 414; AT: 139
20250507 | May | 2030 |  | 5913 | 558 |  | 5912 | 558 | 2602 | 72 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2530 | NA | 1 | 0 | 1 | -72 | 1 | AT: 417; AT: 139
20250507 | May | 2130 |  | 7106 | 690 |  | 7106 | 690 | 1946 | 335 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1611 | NA | 0 | 0 | 0 | -335 | 1 | AT: 404; AT: 159
20250507 | May | 2230 |  | 7164 | 695 |  | 7163 | 695 | 1946 | 393 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1553 | NA | 1 | 0 | 1 | -393 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; FR: 3612; FR: Process fail during TSO validation phase
20250507 | May | 2330 |  | 6584 | 720 |  | 6576 | 720 | 2495 | 393 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2102 | NA | 8 | 0 | 8 | -393 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; FR: 3612; FR: Process fail during TSO validation phase
20250508 | May | 30 |  | 7777 | 727 |  | 7686 | 727 | 2163 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2001 | NA | 91 | 0 | 91 | -162 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border; FR: 3612; FR: Process fail during TSO validation phase
20250508 | May | 130 |  | 7777 | 727 |  | 7686 | 727 | 2163 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2001 | NA | 91 | 0 | 91 | -162 | 1 | AT: 371; AT: 159
20250508 | May | 230 |  | 7777 | 727 |  | 7686 | 727 | 2163 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2001 | NA | 91 | 0 | 91 | -162 | 1 | AT: 371; AT: 159
20250508 | May | 330 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2425 | 1 | AT: 371; AT: 159
20250508 | May | 430 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2425 | 1 | AT: 371; AT: 159
20250508 | May | 530 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2425 | 1 | AT: 372; AT: 140
20250508 | May | 630 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2425 | 1 | AT: 372; AT: 140
20250508 | May | 730 |  | 7235 | 625 |  | 7234 | 625 | -3196 | -3196 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 3196 | 1 | AT: 324; AT: 140
20250508 | May | 830 |  | 7235 | 625 |  | 7234 | 625 | -3196 | -3196 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 3196 | 1 | AT: 321; AT: 140
20250508 | May | 930 | 6799 |  |  | 6250 |  |  | 3249 | 219 | 3579 | Minimum Margin | Validation phase | 3030 | 549 | NA | NA | NA | 6939 | 1 | AT: 321; AT: 140
20250508 | May | 1030 | 6740 |  |  | 6250 |  |  | 3249 | 160 | 3579 | Minimum Margin | Validation phase | 3089 | 490 | NA | NA | NA | 6998 | 1 | AT: 321; AT: 140
20250508 | May | 1130 | 6740 |  |  | 6250 |  |  | 3249 | 160 | 3579 | Minimum Margin | Validation phase | 3089 | 490 | NA | NA | NA | 6998 | 1 | AT: 321; AT: 140
20250508 | May | 1230 | 6741 |  |  | 6250 |  |  | 4029 | 161 | 4359 | Minimum Margin | Validation phase | 3868 | 491 | NA | NA | NA | 8557 | 1 | AT: 321; AT: 140
20250508 | May | 1330 | 6741 |  |  | 6250 |  |  | 4029 | 161 | 4359 | Minimum Margin | Validation phase | 3868 | 491 | NA | NA | NA | 8557 | 1 | AT: 321; AT: 140
20250508 | May | 1430 | 6741 |  |  | 6250 |  |  | 4029 | 161 | 4359 | Minimum Margin | Validation phase | 3868 | 491 | NA | NA | NA | 8557 | 1 | AT: 321; AT: 140
20250508 | May | 1530 | 6743 |  |  | 6250 |  |  | 3332 | 163 | 3662 | Minimum Margin | Validation phase | 3169 | 493 | NA | NA | NA | 7161 | 1 | AT: 321; AT: 140
20250508 | May | 1630 | 6739 |  |  | 6250 |  |  | 3332 | 159 | 3662 | Minimum Margin | Validation phase | 3173 | 489 | NA | NA | NA | 7165 | 1 | AT: 313; AT: 140
20250508 | May | 1730 | 6739 |  |  | 6250 |  |  | 3332 | 159 | 3662 | Minimum Margin | Validation phase | 3173 | 489 | NA | NA | NA | 7165 | 1 | AT: 313; AT: 140
20250508 | May | 1830 |  | 6154 | 469 |  | 6085 | 463 | -1598 | -1598 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 69 | 6 | 75 | 1598 | 1 | AT: 313; AT: 140
20250508 | May | 1930 |  | 6154 | 469 |  | 6085 | 463 | -1598 | -1598 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 69 | 6 | 75 | 1598 | 1 | AT: 369; AT: 140
20250508 | May | 2030 |  | 6154 | 469 |  | 6085 | 463 | -1598 | -1598 | 0 | TTC Selection - LTTCImport | Validation phase | 0 | NA | 69 | 6 | 75 | 1598 | 1 | AT: 369; AT: 140
20250508 | May | 2130 |  | 7175 | 614 |  | 7175 | 614 | -2469 | -2469 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2469 | 1 | AT: 355; AT: 160
20250508 | May | 2230 |  | 7175 | 614 |  | 7175 | 614 | -2469 | -2469 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2469 | 1 | AT: 413; AT: 159
20250508 | May | 2330 |  | 6595 | 639 |  | 6595 | 639 | -1823 | -1823 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1823 | 1 | AT: 413; AT: 159
20250509 | May | 30 |  | 7593 | 684 |  | 7593 | 684 | -2597 | -2597 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2597 | 1 | AT: 413; AT: 159
20250509 | May | 130 |  | 7593 | 684 |  | 7593 | 684 | -2597 | -2597 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2597 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250509 | May | 230 |  | 7593 | 684 |  | 7593 | 684 | -2597 | -2597 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2597 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250509 | May | 330 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 2243 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250509 | May | 430 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 2243 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250509 | May | 530 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 2243 | 1 | AT: 368; AT: 140
20250509 | May | 630 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 2243 | 1 | AT: 377; AT: 140
20250509 | May | 730 |  | 7164 | 594 |  | 7163 | 594 | 1295 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1295 | NA | 1 | 0 | 1 | 0 | 1 | AT: 369; AT: 140
20250509 | May | 830 |  | 7316 | 606 |  | 7315 | 606 | 1295 | 152 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1143 | NA | 1 | 0 | 1 | -152 | 1 | AT: 366; AT: 140
20250509 | May | 930 | 7665 |  |  | 7645 |  |  | 5361 | 213 | 5168 | Minimum Margin | Validation phase | 5148 | 20 | NA | NA | NA | 10123 | 1 | AT: 365; AT: 140
20250509 | May | 1030 | 7619 |  |  | 7604 |  |  | 5361 | 167 | 5209 | Minimum Margin | Validation phase | 5194 | 15 | NA | NA | NA | 10251 | 1 | AT: 405; AT: 138
20250509 | May | 1130 | 7603 |  |  | 7590 |  |  | 5361 | 151 | 5223 | Minimum Margin | Validation phase | 5210 | 13 | NA | NA | NA | 10295 | 1 | AT: 405; AT: 138
20250509 | May | 1230 |  | 7825 | 680 |  | 7824 | 680 | -1900 | -1900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1900 | 1 | AT: 405; AT: 138
20250509 | May | 1330 |  | 7825 | 680 |  | 7824 | 680 | -1900 | -1900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1900 | 1 | AT: 416; AT: 140; FR: 3704; FR: Process fail during TSO validation phase
20250509 | May | 1430 |  | 7825 | 680 |  | 7824 | 680 | -1900 | -1900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1900 | 1 | AT: 416; AT: 140; FR: 3704; FR: Process fail during TSO validation phase
20250509 | May | 1530 |  | 8035 | 646 |  | 7968 | 646 | 3037 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2905 | NA | 67 | 0 | 67 | -132 | 1 | AT: 453; AT: 150; FR: 3736; FR: Process fail during TSO validation phase
20250509 | May | 1630 |  | 8035 | 646 |  | 7968 | 646 | 3037 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2905 | NA | 67 | 0 | 67 | -132 | 1 | AT: 378; AT: 150
20250509 | May | 1730 |  | 8165 | 646 |  | 7656 | 646 | 2965 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2833 | NA | 509 | 0 | 509 | -132 | 1 | AT: 378; AT: 150
20250509 | May | 1830 |  | 6219 | 489 |  | 6219 | 489 | -3067 | -3067 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 3067 | 1 | AT: 378; AT: 150
20250509 | May | 1930 |  | 6219 | 489 |  | 6219 | 489 | -3067 | -3067 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 3067 | 1 | AT: 378; AT: 150
20250509 | May | 2030 |  | 6219 | 489 |  | 6219 | 489 | -3067 | -3067 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 3067 | 1 | AT: 378; AT: 150
20250509 | May | 2130 |  | 6219 | 429 |  | 6219 | 429 | -2544 | -2544 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2544 | 1 | AT: 357; AT: 170
20250509 | May | 2230 |  | 6219 | 429 |  | 6219 | 429 | -2544 | -2544 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2544 | 1 | AT: 468; AT: 169
20250509 | May | 2330 |  | 5649 | 454 |  | 5649 | 454 | -1923 | -1923 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1923 | 1 | AT: 468; AT: 169
20250510 | May | 30 |  | 7579 | 690 |  | 7209 | 657 | -2251 | -2251 | 0 | Critical Branch | Validation phase | 0 | NA | 370 | 33 | 403 | 2251 | 1 | AT: 468; AT: 169
20250510 | May | 130 |  | 7579 | 690 |  | 7209 | 657 | -2251 | -2251 | 0 | Critical Branch | Validation phase | 0 | NA | 370 | 33 | 403 | 2251 | 1 | AT: 475; AT: Reduction because NTC over thermal limit on border; AT: 164; AT: Reduction because NTC over thermal limit on border
20250510 | May | 230 |  | 7579 | 690 |  | 7209 | 657 | -2251 | -2251 | 0 | Critical Branch | Validation phase | 0 | NA | 370 | 33 | 403 | 2251 | 1 | AT: 475; AT: Reduction because NTC over thermal limit on border; AT: 164; AT: Reduction because NTC over thermal limit on border
20250510 | May | 330 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | 0 | NA | 245 | 18 | 263 | 3598 | 1 | AT: 475; AT: Reduction because NTC over thermal limit on border; AT: 164; AT: Reduction because NTC over thermal limit on border
20250510 | May | 430 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | 0 | NA | 245 | 18 | 263 | 3598 | 1 | AT: 475; AT: Reduction because NTC over thermal limit on border; AT: 164; AT: Reduction because NTC over thermal limit on border
20250510 | May | 530 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | 0 | NA | 245 | 18 | 263 | 3598 | 1 | AT: 483; AT: 148
20250510 | May | 630 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | 0 | NA | 245 | 18 | 263 | 3598 | 1 | AT: 483; AT: 148
20250510 | May | 730 |  | 8123 | 700 |  | 8123 | 700 | -2557 | -2557 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2557 | 1 | AT: 424; AT: 150
20250510 | May | 830 |  | 8123 | 700 |  | 8123 | 700 | -2557 | -2557 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2557 | 1 | AT: 424; AT: 150
20250510 | May | 930 | 7535 |  |  | 7535 |  |  | -4021 | -4021 | -4020 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 424; AT: 150
20250510 | May | 1030 | 7535 |  |  | 7535 |  |  | -4021 | -4021 | -4020 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 150
20250510 | May | 1130 | 7535 |  |  | 7535 |  |  | -4021 | -4021 | -4020 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 150
20250510 | May | 1230 | 6645 |  |  | 6645 |  |  | -1103 | -1103 | -1103 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 378; AT: 150
20250510 | May | 1330 | 6645 |  |  | 6645 |  |  | -1103 | -1103 | -1103 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 150
20250510 | May | 1430 | 6645 |  |  | 6645 |  |  | -1103 | -1103 | -1103 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 150
20250510 | May | 1530 | 7523 |  |  | 7523 |  |  | -2299 | -2299 | -2299 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 423; AT: 150
20250510 | May | 1630 | 7523 |  |  | 7523 |  |  | -2299 | -2299 | -2299 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: 150
20250510 | May | 1730 | 7523 |  |  | 7523 |  |  | -2299 | -2299 | -2299 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 450; AT: 150
20250510 | May | 1830 |  | 7531 | 599 |  | 7531 | 599 | -2307 | -2307 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2307 | 1 | AT: 450; AT: 150
20250510 | May | 1930 |  | 7531 | 599 |  | 7531 | 599 | -2307 | -2307 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2307 | 1 | AT: 461; AT: 150
20250510 | May | 2030 |  | 7531 | 599 |  | 7531 | 599 | -2307 | -2307 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2307 | 1 | AT: 461; AT: 150
20250510 | May | 2130 | 8269 |  |  | 8268 |  |  | -2429 | -2429 | -2428 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 445; AT: 170
20250510 | May | 2230 | 8269 |  |  | 8268 |  |  | -2429 | -2429 | -2428 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250510 | May | 2330 | 7664 |  |  | 7664 |  |  | -1811 | -1811 | -1810 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250511 | May | 30 |  | 8518 | 787 |  | 8473 | 787 | -2896 | -2896 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 45 | 0 | 45 | 2896 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250511 | May | 130 |  | 8518 | 787 |  | 8473 | 787 | -2896 | -2896 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 45 | 0 | 45 | 2896 | 1 | AT: 356; AT: 160; FR: 2923; FR: Process fail during TSO validation phase
20250511 | May | 230 |  | 8518 | 787 |  | 8043 | 787 | -2896 | -2896 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 475 | 0 | 475 | 2896 | 1 | AT: 356; AT: 160; FR: 2923; FR: Process fail during TSO validation phase
20250511 | May | 330 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1070 | NA | 100 | 0 | 100 | -109 | 1 | AT: 356; AT: 160; FR: 2923; FR: Process fail during TSO validation phase
20250511 | May | 430 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1070 | NA | 100 | 0 | 100 | -109 | 1 | AT: 356; AT: 160; FR: 2923; FR: Process fail during TSO validation phase
20250511 | May | 530 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1070 | NA | 100 | 0 | 100 | -109 | 1 | AT: 415; AT: 160
20250511 | May | 630 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1070 | NA | 100 | 0 | 100 | -109 | 1 | AT: 415; AT: 160
20250511 | May | 730 | 8150 |  |  | 8150 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 160
20250511 | May | 830 | 8150 |  |  | 8150 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 371; AT: 160
20250511 | May | 930 | 7222 |  |  | 7221 |  |  | -952 | -952 | -951 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 371; AT: 160
20250511 | May | 1030 | 7222 |  |  | 7221 |  |  | -952 | -952 | -951 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 340; AT: 160
20250511 | May | 1130 | 7222 |  |  | 7221 |  |  | -952 | -952 | -951 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 340; AT: 160
20250511 | May | 1230 | 6563 |  |  | 6562 |  |  | -939 | -939 | -939 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 340; AT: 160
20250511 | May | 1330 | 6563 |  |  | 6562 |  |  | -939 | -939 | -939 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 357; AT: 160
20250511 | May | 1430 | 6563 |  |  | 6562 |  |  | -939 | -939 | -939 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 357; AT: 160
20250511 | May | 1530 | 6923 |  |  | 6922 |  |  | -3373 | -3373 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 357; AT: 160
20250511 | May | 1630 | 6923 |  |  | 6922 |  |  | -3373 | -3373 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 401; AT: 160; FR: 3474; FR: Process fail during TSO validation phase
20250511 | May | 1730 | 6923 |  |  | 6922 |  |  | -3373 | -3373 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 401; AT: 160; FR: 3474; FR: Process fail during TSO validation phase
20250511 | May | 1830 |  | 7351 | 663 |  | 7347 | 663 | 1319 | 8 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1311 | NA | 4 | 0 | 4 | -8 | 1 | AT: 401; AT: 160; FR: 3474; FR: Process fail during TSO validation phase
20250511 | May | 1930 |  | 7353 | 663 |  | 7347 | 663 | 1319 | 10 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1309 | NA | 6 | 0 | 6 | -10 | 1 | AT: 394; AT: 160
20250511 | May | 2030 |  | 7353 | 663 |  | 7347 | 663 | 1319 | 10 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1309 | NA | 6 | 0 | 6 | -10 | 1 | AT: 394; AT: 160
20250511 | May | 2130 |  | 7218 | 650 |  | 7217 | 650 | -132 | -132 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 132 | 1 | AT: 394; AT: 160
20250511 | May | 2230 |  | 7218 | 650 |  | 7217 | 650 | -132 | -132 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 132 | 0
20250511 | May | 2330 |  | 7218 | 650 |  | 7217 | 650 | -132 | -132 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 132 | 0
20250512 | May | 30 |  | 5358 | 496 |  | 5358 | 496 | -1354 | -1354 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | 0 | NA | 0 | 0 | 0 | 1354 | 1
20250512 | May | 130 |  | 5358 | 496 |  | 5358 | 496 | -1354 | -1354 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | 0 | NA | 0 | 0 | 0 | 1354 | 0
20250512 | May | 230 |  | 5358 | 496 |  | 5358 | 496 | -1354 | -1354 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | 0 | NA | 0 | 0 | 0 | 1354 | 0
20250512 | May | 330 |  | 6678 | 797 |  | 6678 | 797 | -1742 | -1742 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1742 | 0
20250512 | May | 430 |  | 6678 | 797 |  | 6678 | 797 | -1742 | -1742 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1742 | 0
20250512 | May | 530 |  | 6678 | 797 |  | 6678 | 797 | -1742 | -1742 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1742 | 0
20250512 | May | 630 |  | 6478 | 797 |  | 6478 | 797 | -1499 | -1499 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1499 | 0
20250512 | May | 730 | 6130 |  |  | 6130 |  |  | -2331 | -2331 | -2331 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250512 | May | 830 | 6130 |  |  | 6130 |  |  | -2331 | -2331 | -2331 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250512 | May | 930 | 7695 |  |  | 7630 |  |  | -2107 | -2107 | -2042 | Critical Branch | Smoothing ramp | 0 | 65 | NA | NA | NA | 0 | 1
20250512 | May | 1030 | 7695 |  |  | 7695 |  |  | -2107 | -2107 | -2107 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250512 | May | 1130 | 7695 |  |  | 7630 |  |  | -2107 | -2107 | -2042 | Critical Branch | Smoothing ramp | 0 | 65 | NA | NA | NA | 0 | 1
20250512 | May | 1230 | 6130 |  |  | 6130 |  |  | -2446 | -2446 | -2446 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1330 | 6130 |  |  | 6130 |  |  | -2446 | -2446 | -2446 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1430 | 6130 |  |  | 6130 |  |  | -2446 | -2446 | -2446 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1530 | 7268 |  |  | 7268 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1630 | 7268 |  |  | 7268 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1730 | 7268 |  |  | 7268 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1830 | 6306 |  |  | 6305 |  |  | 5135 | 26 | 5110 | Minimum Margin | Validation phase | 5109 | 1 | NA | NA | NA | 10194 | 1 | CH: 6055; CH: Reduction due to missing redispatch potential
20250512 | May | 1930 | 6289 |  |  | 6289 |  |  | 5135 | 9 | 5126 | Minimum Margin | Minimum Margin | 5126 | 0 | NA | NA | NA | 10243 | 0
20250512 | May | 2030 | 6291 |  |  | 6291 |  |  | 5135 | 11 | 5124 | Minimum Margin | Minimum Margin | 5124 | 0 | NA | NA | NA | 10237 | 0
20250512 | May | 2130 | 7869 |  |  | 7791 |  |  | 5707 | 9 | 5776 | Minimum Margin | Smoothing ramp | 5698 | 78 | NA | NA | NA | 11543 | 1
20250512 | May | 2230 | 7867 |  |  | 7867 |  |  | 5707 | 7 | 5700 | Minimum Margin | Minimum Margin | 5700 | 0 | NA | NA | NA | 11393 | 0
20250512 | May | 2330 | 7422 |  |  | 7412 |  |  | 6037 | 162 | 5885 | Minimum Margin | Validation phase | 5875 | 10 | NA | NA | NA | 11608 | 1 | CH: 7162; CH: Reduction due to missing redispatch potential
20250513 | May | 30 | 5891 |  |  | 5878 |  |  | 2714 | 111 | 2616 | Minimum Margin | Validation phase | 2603 | 13 | NA | NA | NA | 5121 | 0
20250513 | May | 130 | 5891 |  |  | 5878 |  |  | 2714 | 111 | 2616 | Minimum Margin | Validation phase | 2603 | 13 | NA | NA | NA | 5121 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250513 | May | 230 | 5891 |  |  | 5878 |  |  | 2714 | 111 | 2616 | Minimum Margin | Validation phase | 2603 | 13 | NA | NA | NA | 5121 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250513 | May | 330 |  | 5506 | 394 |  | 5445 | 394 | 1427 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1313 | NA | 61 | 0 | 61 | -114 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250513 | May | 430 |  | 5506 | 394 |  | 5445 | 394 | 1427 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1313 | NA | 61 | 0 | 61 | -114 | 1 | FR: 2568; FR: Process fail during TSO validation phase
20250513 | May | 530 |  | 5506 | 394 |  | 5445 | 394 | 1427 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1313 | NA | 61 | 0 | 61 | -114 | 0
20250513 | May | 630 |  | 5349 | 398 |  | 5263 | 398 | 1485 | 157 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1328 | NA | 86 | 0 | 86 | -157 | 0
20250513 | May | 730 | 6380 |  |  | 6368 |  |  | 6148 | 214 | 5946 | Minimum Margin | Validation phase | 5934 | 12 | NA | NA | NA | 11678 | 0
20250513 | May | 830 | 6383 |  |  | 6368 |  |  | 6148 | 217 | 5946 | Minimum Margin | Validation phase | 5931 | 15 | NA | NA | NA | 11675 | 0
20250513 | May | 930 | 8300 |  |  | 7868 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 432 | NA | NA | NA | 0 | 1
20250513 | May | 1030 | 8300 |  |  | 8300 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250513 | May | 1130 | 8300 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 550 | NA | NA | NA | 0 | 1
20250513 | May | 1230 | 6279 |  |  | 6250 |  |  | 4525 | 149 | 4405 | Minimum Margin | Validation phase | 4376 | 29 | NA | NA | NA | 8661 | 0
20250513 | May | 1330 | 6280 |  |  | 6250 |  |  | 4525 | 150 | 4405 | Minimum Margin | Validation phase | 4375 | 30 | NA | NA | NA | 8660 | 0
20250513 | May | 1430 | 6279 |  |  | 6250 |  |  | 4525 | 149 | 4405 | Minimum Margin | Validation phase | 4376 | 29 | NA | NA | NA | 8661 | 0
20250513 | May | 1530 | 6283 |  |  | 6250 |  |  | 2698 | 153 | 2578 | Minimum Margin | Validation phase | 2545 | 33 | NA | NA | NA | 5003 | 0
20250513 | May | 1630 | 6283 |  |  | 6250 |  |  | 2698 | 153 | 2578 | Minimum Margin | Validation phase | 2545 | 33 | NA | NA | NA | 5003 | 0
20250513 | May | 1730 | 6283 |  |  | 6250 |  |  | 2698 | 153 | 2578 | Minimum Margin | Validation phase | 2545 | 33 | NA | NA | NA | 5003 | 0
20250513 | May | 1830 | 6683 |  |  | 6485 |  |  | 2597 | 403 | 2392 | Minimum Margin | Validation phase | 2194 | 198 | NA | NA | NA | 4381 | 0
20250513 | May | 1930 | 6683 |  |  | 6485 |  |  | 2597 | 403 | 2392 | Minimum Margin | Validation phase | 2194 | 198 | NA | NA | NA | 4381 | 0
20250513 | May | 2030 | 6459 |  |  | 6459 |  |  | 2597 | 179 | 2418 | Minimum Margin | Minimum Margin | 2418 | 0 | NA | NA | NA | 4657 | 0
20250513 | May | 2130 | 6680 |  |  | 6680 |  |  | 3535 | 400 | 3135 | Minimum Margin | Minimum Margin | 3135 | 0 | NA | NA | NA | 5870 | 0
20250513 | May | 2230 | 6680 |  |  | 6680 |  |  | 3535 | 400 | 3135 | Minimum Margin | Minimum Margin | 3135 | 0 | NA | NA | NA | 5870 | 0
20250513 | May | 2330 | 6078 |  |  | 6078 |  |  | 4075 | 398 | 3677 | Minimum Margin | Minimum Margin | 3677 | 0 | NA | NA | NA | 6956 | 0
20250514 | May | 30 | 5780 |  |  | 5780 |  |  | -1510 | -1510 | -1510 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 130 | 5780 |  |  | 5780 |  |  | -1510 | -1510 | -1510 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 230 | 5780 |  |  | 5780 |  |  | -1510 | -1510 | -1510 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 330 | 5780 |  |  | 5780 |  |  | -1256 | -1256 | -1256 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 430 | 5780 |  |  | 5780 |  |  | -1256 | -1256 | -1256 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 530 | 5780 |  |  | 5780 |  |  | -1256 | -1256 | -1256 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 630 | 5780 |  |  | 5780 |  |  | -1256 | -1256 | -1256 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 730 | 6280 |  |  | 6280 |  |  | 6133 | 0 | 6133 | TTC Selection - LTTC | TTC Selection - LTTC | 6133 | 0 | NA | NA | NA | 6133 | 0
20250514 | May | 830 | 6280 |  |  | 6280 |  |  | 6133 | 0 | 6133 | TTC Selection - LTTC | TTC Selection - LTTC | 6133 | 0 | NA | NA | NA | 6133 | 0
20250514 | May | 930 | 8125 |  |  | 7563 |  |  | 2267 | 176 | 2653 | Minimum Margin | Validation phase | 2091 | 562 | NA | NA | NA | 5130 | 1 | CH: 7313; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1030 | 8106 |  |  | 7563 |  |  | 2267 | 157 | 2653 | Minimum Margin | Validation phase | 2110 | 543 | NA | NA | NA | 5149 | 1 | CH: 7313; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1130 | 8106 |  |  | 7563 |  |  | 2267 | 157 | 2653 | Minimum Margin | Validation phase | 2110 | 543 | NA | NA | NA | 5149 | 1 | CH: 7313; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1230 | 7556 |  |  | 7556 |  |  | -2132 | -2132 | -2132 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 1330 | 7556 |  |  | 7556 |  |  | -2132 | -2132 | -2132 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 1430 | 7556 |  |  | 7556 |  |  | -2132 | -2132 | -2132 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250514 | May | 1530 | 8142 |  |  | 7568 |  |  | -1893 | -1893 | -1319 | Critical Branch | Validation phase | 0 | 574 | NA | NA | NA | 0 | 1 | CH: 7318; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1630 | 8142 |  |  | 7568 |  |  | -1893 | -1893 | -1319 | Critical Branch | Validation phase | 0 | 574 | NA | NA | NA | 0 | 1 | CH: 7318; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1730 | 8142 |  |  | 7568 |  |  | -1893 | -1893 | -1319 | Critical Branch | Validation phase | 0 | 574 | NA | NA | NA | 0 | 1 | CH: 7318; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1830 |  | 6010 | 418 |  | 6010 | 418 | 1705 | 152 | 0 | Minimum Margin | Minimum Margin | 1553 | NA | 0 | 0 | 0 | -152 | 0
20250514 | May | 1930 |  | 5858 | 405 |  | 5858 | 405 | 1705 | 0 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 1705 | NA | 0 | 0 | 0 | 0 | 0
20250514 | May | 2030 |  | 5991 | 416 |  | 5991 | 416 | 1705 | 133 | 0 | Minimum Margin | Minimum Margin | 1572 | NA | 0 | 0 | 0 | -133 | 0
20250514 | May | 2130 |  | 5944 | 449 |  | 5944 | 449 | 1972 | 86 | 0 | Minimum Margin | Minimum Margin | 1886 | NA | 0 | 0 | 0 | -86 | 0
20250514 | May | 2230 |  | 6282 | 477 |  | 6282 | 477 | 1972 | 423 | 0 | Minimum Margin | Minimum Margin | 1549 | NA | 0 | 0 | 0 | -423 | 1 | FR: 2810; FR: Process fail during TSO validation phase
20250514 | May | 2330 |  | 5438 | 479 |  | 5436 | 479 | 2538 | 140 | 0 | Minimum Margin | Minimum Margin | 2398 | NA | 2 | 0 | 2 | -140 | 1 | FR: 2810; FR: Process fail during TSO validation phase
20250515 | May | 30 |  | 6247 | 588 |  | 6007 | 588 | 900 | 454 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 446 | NA | 240 | 0 | 240 | -454 | 1 | FR: 2810; FR: Process fail during TSO validation phase
20250515 | May | 130 |  | 6247 | 588 |  | 6007 | 588 | 900 | 454 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 446 | NA | 240 | 0 | 240 | -454 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250515 | May | 230 |  | 6247 | 588 |  | 6007 | 588 | 900 | 454 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 446 | NA | 240 | 0 | 240 | -454 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250515 | May | 330 |  | 5507 | 503 |  | 5446 | 503 | 2334 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2218 | NA | 61 | 0 | 61 | -116 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250515 | May | 430 |  | 5507 | 503 |  | 5446 | 503 | 2334 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2218 | NA | 61 | 0 | 61 | -116 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250515 | May | 530 |  | 5507 | 503 |  | 5446 | 503 | 2334 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2218 | NA | 61 | 0 | 61 | -116 | 0
20250515 | May | 630 |  | 5507 | 503 |  | 5446 | 503 | 2334 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2218 | NA | 61 | 0 | 61 | -116 | 0
20250515 | May | 730 | 6712 |  |  | 6485 |  |  | 1698 | 432 | 1493 | Minimum Margin | Validation phase | 1266 | 227 | NA | NA | NA | 2554 | 0
20250515 | May | 830 | 6626 |  |  | 6485 |  |  | 1698 | 346 | 1493 | Minimum Margin | Validation phase | 1352 | 141 | NA | NA | NA | 2640 | 0
20250515 | May | 930 | 6454 |  |  | 6442 |  |  | 4420 | 174 | 4258 | Minimum Margin | Validation phase | 4246 | 12 | NA | NA | NA | 8342 | 1 | CH: 6192; CH: Reduction due to missing redispatch potential
20250515 | May | 1030 | 6437 |  |  | 6427 |  |  | 4420 | 157 | 4273 | Minimum Margin | Validation phase | 4263 | 10 | NA | NA | NA | 8389 | 1 | CH: 6177; CH: Reduction due to missing redispatch potential
20250515 | May | 1130 | 6437 |  |  | 6427 |  |  | 4420 | 157 | 4273 | Minimum Margin | Validation phase | 4263 | 10 | NA | NA | NA | 8389 | 1 | CH: 6177; CH: Reduction due to missing redispatch potential
20250515 | May | 1230 | 7550 |  |  | 7550 |  |  | -1082 | -1082 | -1082 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250515 | May | 1330 | 7550 |  |  | 7550 |  |  | -1082 | -1082 | -1082 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250515 | May | 1430 | 7550 |  |  | 7550 |  |  | -1082 | -1082 | -1082 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250515 | May | 1530 | 7768 |  |  | 7768 |  |  | -1149 | -1149 | -1149 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250515 | May | 1630 | 7768 |  |  | 7768 |  |  | -1149 | -1149 | -1149 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250515 | May | 1730 | 7768 |  |  | 7768 |  |  | -1149 | -1149 | -1149 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250515 | May | 1830 | 6444 |  |  | 6435 |  |  | 3623 | 164 | 3468 | Minimum Margin | Validation phase | 3459 | 9 | NA | NA | NA | 6772 | 1 | CH: 6185; CH: Reduction due to missing redispatch potential
20250515 | May | 1930 | 6444 |  |  | 6435 |  |  | 3623 | 164 | 3468 | Minimum Margin | Validation phase | 3459 | 9 | NA | NA | NA | 6772 | 1 | CH: 6185; CH: Reduction due to missing redispatch potential
20250515 | May | 2030 | 6444 |  |  | 6435 |  |  | 3623 | 164 | 3468 | Minimum Margin | Validation phase | 3459 | 9 | NA | NA | NA | 6772 | 1 | CH: 6185; CH: Reduction due to missing redispatch potential
20250515 | May | 2130 | 6650 |  |  | 6650 |  |  | 1187 | 370 | 817 | Minimum Margin | Minimum Margin | 817 | 0 | NA | NA | NA | 1264 | 0
20250515 | May | 2230 | 6595 |  |  | 6595 |  |  | 1187 | 315 | 872 | Minimum Margin | Minimum Margin | 872 | 0 | NA | NA | NA | 1429 | 0
20250515 | May | 2330 | 6114 |  |  | 6114 |  |  | 1757 | 434 | 1323 | Minimum Margin | Minimum Margin | 1323 | 0 | NA | NA | NA | 2212 | 0
20250516 | May | 30 | 6914 |  |  | 6905 |  |  | 2091 | 128 | 1972 | Minimum Margin | Validation phase | 1963 | 9 | NA | NA | NA | 3816 | 0
20250516 | May | 130 | 6931 |  |  | 6921 |  |  | 2091 | 145 | 1956 | Minimum Margin | Validation phase | 1946 | 10 | NA | NA | NA | 3767 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250516 | May | 230 | 6931 |  |  | 6921 |  |  | 2091 | 145 | 1956 | Minimum Margin | Validation phase | 1946 | 10 | NA | NA | NA | 3767 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250516 | May | 330 |  | 5535 | 482 |  | 5459 | 482 | 2132 | 144 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1988 | NA | 76 | 0 | 76 | -144 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250516 | May | 430 |  | 5535 | 482 |  | 5459 | 482 | 2132 | 144 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1988 | NA | 76 | 0 | 76 | -144 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250516 | May | 530 |  | 5535 | 482 |  | 5459 | 482 | 2132 | 144 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1988 | NA | 76 | 0 | 76 | -144 | 0
20250516 | May | 630 |  | 5554 | 483 |  | 5468 | 483 | 2132 | 163 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1969 | NA | 86 | 0 | 86 | -163 | 0
20250516 | May | 730 | 7282 |  |  | 7282 |  |  | -87 | -87 | -87 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250516 | May | 830 | 7282 |  |  | 7282 |  |  | -87 | -87 | -87 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250516 | May | 930 | 6426 |  |  | 6250 |  |  | 2855 | 146 | 2885 | Minimum Margin | Validation phase | 2709 | 176 | NA | NA | NA | 5624 | 0
20250516 | May | 1030 | 6426 |  |  | 6250 |  |  | 2855 | 146 | 2885 | Minimum Margin | Validation phase | 2709 | 176 | NA | NA | NA | 5624 | 0
20250516 | May | 1130 | 6426 |  |  | 6250 |  |  | 2855 | 146 | 2885 | Minimum Margin | Validation phase | 2709 | 176 | NA | NA | NA | 5624 | 0
20250516 | May | 1230 | 7926 |  |  | 6848 |  |  | 3769 | 143 | 4704 | Minimum Margin | Validation phase | 3626 | 1078 | NA | NA | NA | 9265 | 0
20250516 | May | 1330 | 7926 |  |  | 6848 |  |  | 3769 | 143 | 4704 | Minimum Margin | Validation phase | 3626 | 1078 | NA | NA | NA | 9265 | 0
20250516 | May | 1430 | 7926 |  |  | 6848 |  |  | 3769 | 143 | 4704 | Minimum Margin | Validation phase | 3626 | 1078 | NA | NA | NA | 9265 | 0
20250516 | May | 1530 | 6416 |  |  | 6250 |  |  | 3497 | 136 | 3527 | Minimum Margin | Validation phase | 3361 | 166 | NA | NA | NA | 6918 | 0
20250516 | May | 1630 | 6416 |  |  | 6250 |  |  | 3497 | 136 | 3527 | Minimum Margin | Validation phase | 3361 | 166 | NA | NA | NA | 6918 | 0
20250516 | May | 1730 | 6723 |  |  | 6250 |  |  | 3547 | 143 | 3877 | Minimum Margin | Validation phase | 3404 | 473 | NA | NA | NA | 7611 | 0
20250516 | May | 1830 | 6743 |  |  | 6731 |  |  | 3993 | 163 | 3842 | Minimum Margin | Validation phase | 3830 | 12 | NA | NA | NA | 7521 | 0
20250516 | May | 1930 | 6743 |  |  | 6731 |  |  | 3993 | 163 | 3842 | Minimum Margin | Validation phase | 3830 | 12 | NA | NA | NA | 7521 | 0
20250516 | May | 2030 | 6743 |  |  | 6731 |  |  | 3993 | 163 | 3842 | Minimum Margin | Validation phase | 3830 | 12 | NA | NA | NA | 7521 | 0
20250516 | May | 2130 |  | 8025 | 655 |  | 7948 | 655 | -2086 | -2086 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 77 | 0 | 77 | 2086 | 1
20250516 | May | 2230 |  | 8025 | 655 |  | 8025 | 655 | -2086 | -2086 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 2086 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250516 | May | 2330 |  | 7445 | 680 |  | 7445 | 680 | -1493 | -1493 | 0 | Critical Branch | Min import NTC Threshold | 0 | NA | 0 | 0 | 0 | 1493 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250517 | May | 30 |  | 5888 | 426 |  | 5786 | 426 | 1412 | 201 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1211 | NA | 102 | 0 | 102 | -201 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250517 | May | 130 |  | 5885 | 426 |  | 5785 | 426 | 1412 | 197 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1215 | NA | 100 | 0 | 100 | -197 | 1 | FR: 3498
20250517 | May | 230 |  | 5859 | 423 |  | 5772 | 423 | 1412 | 172 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1240 | NA | 87 | 0 | 87 | -172 | 1 | FR: 3498
20250517 | May | 330 | 8150 |  |  | 7665 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 485 | NA | NA | NA | 0 | 1 | FR: 3498
20250517 | May | 430 | 8150 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 119 | NA | NA | NA | 0 | 1 | FR: 3498
20250517 | May | 530 | 8150 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 119 | NA | NA | NA | 0 | 1 | FR: 3727
20250517 | May | 630 | 8150 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 119 | NA | NA | NA | 0 | 1 | FR: 3727
20250517 | May | 730 | 8750 |  |  | 8633 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 117 | NA | NA | NA | 0 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250517 | May | 830 | 8750 |  |  | 8183 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 567 | NA | NA | NA | 0 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250517 | May | 930 |  | 6362 | 400 |  | 6258 | 400 | 3346 | 208 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3138 | NA | 104 | 0 | 104 | -208 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250517 | May | 1030 |  | 6298 | 395 |  | 6225 | 395 | 3346 | 143 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3203 | NA | 73 | 0 | 73 | -143 | 1 | FR: 3452
20250517 | May | 1130 |  | 6298 | 395 |  | 6225 | 395 | 3346 | 143 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3203 | NA | 73 | 0 | 73 | -143 | 1 | FR: 3452
20250517 | May | 1230 | 8160 |  |  | 7025 |  |  | -2079 | -2079 | -944 | Critical Branch | Validation phase | 0 | 1135 | NA | NA | NA | 0 | 1 | CH: 6775; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 3452
20250517 | May | 1330 | 8160 |  |  | 7025 |  |  | -2079 | -2079 | -944 | Critical Branch | Validation phase | 0 | 1135 | NA | NA | NA | 0 | 1 | CH: 6775; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2716; FR: Process fail during TSO validation phase
20250517 | May | 1430 | 8160 |  |  | 7025 |  |  | -2079 | -2079 | -944 | Critical Branch | Validation phase | 0 | 1135 | NA | NA | NA | 0 | 1 | CH: 6775; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia; FR: 2716; FR: Process fail during TSO validation phase
20250517 | May | 1530 | 6788 |  |  | 6565 |  |  | 5936 | 208 | 6173 | Minimum Margin | Validation phase | 5728 | 223 | NA | NA | NA | 12138 | 1 | CH: 6521; CH: Reduction due to missing redispatch potential; FR: 2716; FR: Process fail during TSO validation phase
20250517 | May | 1630 | 6785 |  |  | 6563 |  |  | 5936 | 205 | 6173 | Minimum Margin | Validation phase | 5731 | 222 | NA | NA | NA | 12141 | 1 | CH: 6518; CH: Reduction due to missing redispatch potential; FR: 2716; FR: Process fail during TSO validation phase
20250517 | May | 1730 | 6739 |  |  | 6542 |  |  | 5936 | 159 | 6174 | Minimum Margin | Validation phase | 5777 | 197 | NA | NA | NA | 12189 | 1 | CH: 6477; CH: Reduction due to missing redispatch potential; FR: 2716; FR: Process fail during TSO validation phase
20250517 | May | 1830 | 6738 |  |  | 6541 |  |  | 1866 | 158 | 2105 | Minimum Margin | Validation phase | 1708 | 197 | NA | NA | NA | 4052 | 1 | CH: 6475; CH: Reduction due to missing redispatch potential; FR: 2716
20250517 | May | 1930 | 6789 |  |  | 6566 |  |  | 1866 | 209 | 2104 | Minimum Margin | Validation phase | 1657 | 223 | NA | NA | NA | 3999 | 1 | CH: 6522; CH: Reduction due to missing redispatch potential; FR: 2832; FR: Process fail during TSO validation phase
20250517 | May | 2030 | 6580 |  |  | 6463 |  |  | 1866 | 0 | 2109 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 1866 | 117 | NA | NA | NA | 4218 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250517 | May | 2130 |  | 6289 | 389 |  | 6221 | 389 | 2666 | 135 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2531 | NA | 68 | 0 | 68 | -135 | 1 | FR: 2591; FR: Process fail during TSO validation phase
20250517 | May | 2230 |  | 6289 | 389 |  | 6221 | 389 | 2666 | 135 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2531 | NA | 68 | 0 | 68 | -135 | 0
20250517 | May | 2330 |  | 5729 | 414 |  | 5660 | 414 | 3118 | 135 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2983 | NA | 69 | 0 | 69 | -135 | 0
20250518 | May | 30 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 130 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 230 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 330 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 430 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 530 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 630 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 730 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 830 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 930 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1030 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1130 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1230 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1330 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1430 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1530 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1630 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1730 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1830 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1930 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 2030 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 2130 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 2230 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7405; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2638; FR: Process fail during TSO validation phase
20250518 | May | 2330 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | CH: 7400; CH: IT issues in internal Validation Tool. BackUp-NTC-values are applied.; FR: 2638; FR: Process fail during TSO validation phase
20250519 | May | 30 |  | 5743 | 464 |  | 5715 | 464 | 1402 | 55 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1347 | NA | 28 | 0 | 28 | -55 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250519 | May | 130 |  | 5743 | 464 |  | 5715 | 464 | 1402 | 55 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1347 | NA | 28 | 0 | 28 | -55 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250519 | May | 230 |  | 5743 | 464 |  | 5715 | 464 | 1402 | 55 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1347 | NA | 28 | 0 | 28 | -55 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250519 | May | 330 |  | 5816 | 394 |  | 5751 | 394 | 1899 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1770 | NA | 65 | 0 | 65 | -129 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250519 | May | 430 |  | 5816 | 394 |  | 5751 | 394 | 1899 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1770 | NA | 65 | 0 | 65 | -129 | 1 | FR: 2638; FR: Process fail during TSO validation phase
20250519 | May | 530 |  | 5816 | 394 |  | 5751 | 394 | 1899 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1770 | NA | 65 | 0 | 65 | -129 | 0
20250519 | May | 630 |  | 5816 | 394 |  | 5751 | 394 | 1899 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1770 | NA | 65 | 0 | 65 | -129 | 0
20250519 | May | 730 | 6393 |  |  | 6250 |  |  | 5708 | 113 | 5738 | Minimum Margin | Validation phase | 5595 | 143 | NA | NA | NA | 11363 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 830 | 6512 |  |  | 6250 |  |  | 5708 | 232 | 5738 | Minimum Margin | Validation phase | 5476 | 262 | NA | NA | NA | 11244 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 930 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1030 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1130 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1230 | 6446 |  |  | 6250 |  |  | 6550 | 166 | 6580 | Minimum Margin | Validation phase | 6384 | 196 | NA | NA | NA | 12994 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1330 | 6446 |  |  | 6250 |  |  | 6550 | 166 | 6580 | Minimum Margin | Validation phase | 6384 | 196 | NA | NA | NA | 12994 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1430 | 6446 |  |  | 6250 |  |  | 6550 | 166 | 6580 | Minimum Margin | Validation phase | 6384 | 196 | NA | NA | NA | 12994 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1530 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1630 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1830 | 6280 |  |  | 6280 |  |  | -4215 | -4215 | -4215 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250519 | May | 1930 | 6280 |  |  | 6280 |  |  | -4215 | -4215 | -4215 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250519 | May | 2030 | 6280 |  |  | 6280 |  |  | -4215 | -4215 | -4215 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250519 | May | 2130 |  | 5858 | 473 |  | 5858 | 473 | -1535 | -1535 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1535 | 0
20250519 | May | 2230 |  | 5858 | 473 |  | 5858 | 473 | -1535 | -1535 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1535 | 0
20250519 | May | 2330 |  | 5298 | 498 |  | 5298 | 498 | -920 | -920 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 920 | 0
20250520 | May | 30 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250520 | May | 130 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250520 | May | 230 | 7850 |  |  | 7356 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 494 | NA | NA | NA | 0 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250520 | May | 330 |  | 5553 | 398 |  | 5467 | 398 | 2250 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2088 | NA | 86 | 0 | 86 | -162 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250520 | May | 430 |  | 5492 | 393 |  | 5439 | 393 | 2250 | 100 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2150 | NA | 53 | 0 | 53 | -100 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250520 | May | 530 |  | 5409 | 385 |  | 5399 | 385 | 2250 | 17 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2233 | NA | 10 | 0 | 10 | -17 | 0
20250520 | May | 630 |  | 5407 | 385 |  | 5398 | 385 | 2250 | 15 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2235 | NA | 9 | 0 | 9 | -15 | 0
20250520 | May | 730 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2050 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 830 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2050 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 930 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2050 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1030 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2050 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1130 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2050 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1230 | 6294 |  |  | 6285 |  |  | 3967 | 164 | 3812 | Minimum Margin | Validation phase | 3803 | 9 | NA | NA | NA | 7460 | 0
20250520 | May | 1330 | 6294 |  |  | 6285 |  |  | 3967 | 164 | 3812 | Minimum Margin | Validation phase | 3803 | 9 | NA | NA | NA | 7460 | 0
20250520 | May | 1430 | 6314 |  |  | 6304 |  |  | 3967 | 184 | 3793 | Minimum Margin | Validation phase | 3783 | 10 | NA | NA | NA | 7402 | 0
20250520 | May | 1530 | 8300 |  |  | 6509 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1791 | NA | NA | NA | 0 | 1 | SI: 6259; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1630 | 8300 |  |  | 6509 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1791 | NA | NA | NA | 0 | 1 | SI: 6259; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1730 | 8300 |  |  | 6509 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1791 | NA | NA | NA | 0 | 1 | SI: 6259; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1830 | 6148 |  |  | 6146 |  |  | 6651 | 18 | 6635 | Minimum Margin | Validation phase | 6633 | 2 | NA | NA | NA | 13252 | 0
20250520 | May | 1930 | 6297 |  |  | 6295 |  |  | 6737 | 17 | 6722 | Minimum Margin | Validation phase | 6720 | 2 | NA | NA | NA | 13427 | 0
20250520 | May | 2030 | 6297 |  |  | 6295 |  |  | 6737 | 17 | 6722 | Minimum Margin | Validation phase | 6720 | 2 | NA | NA | NA | 13427 | 0
20250520 | May | 2130 |  | 6291 | 525 |  | 6291 | 525 | -2405 | -2405 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2405 | 0
20250520 | May | 2230 |  | 6291 | 525 |  | 6291 | 525 | -2405 | -2405 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2405 | 0
20250520 | May | 2330 |  | 5731 | 550 |  | 5731 | 550 | -1786 | -1786 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1786 | 0
20250521 | May | 30 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 130 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 230 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 430 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 530 | 7850 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 100 | NA | NA | NA | 0 | 1
20250521 | May | 630 | 7850 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1600 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 830 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 930 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1030 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1130 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1230 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1867 | NA | NA | NA | 0 | 1 | SI: 6333; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1330 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1867 | NA | NA | NA | 0 | 1 | SI: 6333; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1430 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1867 | NA | NA | NA | 0 | 1 | SI: 6333; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1530 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1630 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1830 | 8450 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 700 | NA | NA | NA | 0 | 1
20250521 | May | 1930 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 2030 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 2130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 2230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250521 | May | 2330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 30 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 130 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 230 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 430 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 530 | 7850 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 100 | NA | NA | NA | 0 | 1
20250522 | May | 630 | 7850 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1600 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 830 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 930 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1030 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1130 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1230 | 8390 |  |  | 6553 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1837 | NA | NA | NA | 0 | 1 | SI: 6303; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1330 | 8390 |  |  | 6553 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1837 | NA | NA | NA | 0 | 1 | SI: 6303; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1430 | 8390 |  |  | 6553 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1837 | NA | NA | NA | 0 | 1 | SI: 6303; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1530 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2140 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1630 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1830 | 8450 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 700 | NA | NA | NA | 0 | 1
20250522 | May | 1930 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 2030 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 2130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250522 | May | 2230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250522 | May | 2330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250523 | May | 30 |  | 5541 | 397 |  | 5462 | 397 | 3341 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3191 | NA | 79 | 0 | 79 | -150 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250523 | May | 130 |  | 5541 | 397 |  | 5462 | 397 | 3341 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3191 | NA | 79 | 0 | 79 | -150 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250523 | May | 230 |  | 5541 | 397 |  | 5462 | 397 | 3341 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 3191 | NA | 79 | 0 | 79 | -150 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250523 | May | 330 |  | 5542 | 447 |  | 5462 | 447 | 3095 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2945 | NA | 80 | 0 | 80 | -150 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250523 | May | 430 |  | 5542 | 447 |  | 5462 | 447 | 3095 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2945 | NA | 80 | 0 | 80 | -150 | 1 | FR: 2598; FR: Process fail during TSO validation phase
20250523 | May | 530 |  | 5542 | 447 |  | 5462 | 447 | 3095 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2945 | NA | 80 | 0 | 80 | -150 | 0
20250523 | May | 630 |  | 5546 | 448 |  | 5464 | 448 | 3095 | 154 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2941 | NA | 82 | 0 | 82 | -154 | 0
20250523 | May | 730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 830 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 930 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1030 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1130 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 2200 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1230 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1867 | NA | NA | NA | 0 | 1 | SI: 6333; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1330 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1867 | NA | NA | NA | 0 | 1 | SI: 6333; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1430 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1867 | NA | NA | NA | 0 | 1 | SI: 6333; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1530 | 6280 |  |  | 6250 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1630 | 6280 |  |  | 6250 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 30 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1730 | 6580 |  |  | 6250 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | 0 | 330 | NA | NA | NA | 0 | 1 | SI: 6000; SI: Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1830 | 8750 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1000 | NA | NA | NA | 0 | 1
20250523 | May | 1930 | 8750 |  |  | 8750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250523 | May | 2030 | 8750 |  |  | 8154 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 596 | NA | NA | NA | 0 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250523 | May | 2130 |  | 6303 | 441 |  | 6228 | 441 | 5105 | 149 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4956 | NA | 75 | 0 | 75 | -149 | 1 | FR: 2591; FR: Process fail during TSO validation phase
20250523 | May | 2230 |  | 6303 | 441 |  | 6228 | 441 | 5105 | 149 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4956 | NA | 75 | 0 | 75 | -149 | 0
20250523 | May | 2330 |  | 5743 | 466 |  | 5667 | 466 | 5564 | 149 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 5415 | NA | 76 | 0 | 76 | -149 | 0
20250524 | May | 30 | 6085 |  |  | 6085 |  |  | 2012 | 5 | 2007 | Minimum Margin | Minimum Margin | 2007 | 0 | NA | NA | NA | 4009 | 0
20250524 | May | 130 | 6104 |  |  | 6101 |  |  | 2012 | 24 | 1991 | Minimum Margin | Validation phase | 1988 | 3 | NA | NA | NA | 3958 | 1 | CH: 5851; CH: Reduction due to missing redispatch potential
20250524 | May | 230 | 6264 |  |  | 6237 |  |  | 2012 | 184 | 1855 | Minimum Margin | Validation phase | 1828 | 27 | NA | NA | NA | 3526 | 1 | CH: 5987; CH: Reduction due to missing redispatch potential
20250524 | May | 330 | 6241 |  |  | 6229 |  |  | 1697 | 161 | 1548 | Minimum Margin | Validation phase | 1536 | 12 | NA | NA | NA | 2935 | 1 | CH: 5979; CH: Reduction due to missing redispatch potential
20250524 | May | 430 | 6241 |  |  | 6229 |  |  | 1697 | 161 | 1548 | Minimum Margin | Validation phase | 1536 | 12 | NA | NA | NA | 2935 | 1 | CH: 5979; CH: Reduction due to missing redispatch potential
20250524 | May | 530 | 6283 |  |  | 6268 |  |  | 1697 | 203 | 1509 | Minimum Margin | Validation phase | 1494 | 15 | NA | NA | NA | 2815 | 1 | CH: 6018; CH: Reduction due to missing redispatch potential; FR: 2832; FR: Process fail during TSO validation phase
20250524 | May | 630 | 6080 |  |  | 6080 |  |  | 1697 | 0 | 1697 | TTC Selection - LTTC | TTC Selection - LTTC | 1697 | 0 | NA | NA | NA | 1697 | 1 | FR: 2832; FR: Process fail during TSO validation phase
20250524 | May | 730 |  | 6340 | 494 |  | 6246 | 494 | 1126 | 186 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 940 | NA | 94 | 0 | 94 | -186 | 0
20250524 | May | 830 |  | 6226 | 485 |  | 6189 | 485 | 1126 | 72 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1054 | NA | 37 | 0 | 37 | -72 | 0
20250524 | May | 930 | 7952 |  |  | 7945 |  |  | 3421 | 74 | 3354 | Minimum Margin | Validation phase | 3347 | 7 | NA | NA | NA | 6634 | 1 | CH: 7695; CH: Reduction due to missing redispatch potential
20250524 | May | 1030 | 8026 |  |  | 8012 |  |  | 3421 | 148 | 3287 | Minimum Margin | Validation phase | 3273 | 14 | NA | NA | NA | 6426 | 1 | CH: 7762; CH: Reduction due to missing redispatch potential
20250524 | May | 1130 | 8026 |  |  | 8012 |  |  | 3421 | 148 | 3287 | Minimum Margin | Validation phase | 3273 | 14 | NA | NA | NA | 6426 | 1 | CH: 7762; CH: Reduction due to missing redispatch potential
20250524 | May | 1230 | 8147 |  |  | 8147 |  |  | -3419 | -3419 | -3419 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250524 | May | 1330 | 8147 |  |  | 8147 |  |  | -3419 | -3419 | -3419 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250524 | May | 1430 | 8147 |  |  | 8147 |  |  | -3419 | -3419 | -3419 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250524 | May | 1530 | 6795 |  |  | 6774 |  |  | 4432 | 215 | 4238 | Minimum Margin | Validation phase | 4217 | 21 | NA | NA | NA | 8261 | 1 | CH: 6524; CH: Reduction due to missing redispatch potential
20250524 | May | 1630 | 6728 |  |  | 6714 |  |  | 4432 | 148 | 4298 | Minimum Margin | Validation phase | 4284 | 14 | NA | NA | NA | 8448 | 1 | CH: 6464; CH: Reduction due to missing redispatch potential
20250524 | May | 1730 | 6737 |  |  | 6722 |  |  | 4432 | 157 | 4290 | Minimum Margin | Validation phase | 4275 | 15 | NA | NA | NA | 8423 | 1 | CH: 6472; CH: Reduction due to missing redispatch potential
20250524 | May | 1830 | 6580 |  |  | 6580 |  |  | 1804 | 0 | 1804 | TTC Selection - LTTC | TTC Selection - LTTC | 1804 | 0 | NA | NA | NA | 1804 | 0
20250524 | May | 1930 | 6809 |  |  | 6788 |  |  | 1804 | 229 | 1596 | Minimum Margin | Validation phase | 1575 | 21 | NA | NA | NA | 2963 | 1 | CH: 6538; CH: Reduction due to missing redispatch potential
20250524 | May | 2030 | 6580 |  |  | 6580 |  |  | 1804 | 0 | 1804 | TTC Selection - LTTC | TTC Selection - LTTC | 1804 | 0 | NA | NA | NA | 1804 | 0
20250524 | May | 2130 |  | 8069 | 650 |  | 7802 | 650 | -1901 | -1901 | 0 | Critical Branch | Smoothing ramp | 0 | NA | 267 | 0 | 267 | 1901 | 1
20250524 | May | 2230 |  | 8069 | 650 |  | 8069 | 650 | -1901 | -1901 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1901 | 1 | AT: 308; AT: 160
20250524 | May | 2330 |  | 7489 | 675 |  | 7489 | 675 | -1262 | -1262 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1262 | 1 | AT: 308; AT: 160
20250525 | May | 30 |  | 5781 | 521 |  | 5781 | 521 | -508 | -508 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 508 | 1 | AT: 308; AT: 160
20250525 | May | 130 |  | 5781 | 521 |  | 5781 | 521 | -508 | -508 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 508 | 1 | AT: 403; AT: 159
20250525 | May | 230 |  | 5781 | 521 |  | 5781 | 521 | -508 | -508 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 508 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250525 | May | 330 |  | 7718 | 695 |  | 7421 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 297 | 0 | 297 | 1805 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250525 | May | 430 |  | 7718 | 695 |  | 7713 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 5 | 0 | 5 | 1805 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250525 | May | 530 |  | 7718 | 695 |  | 7713 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 5 | 0 | 5 | 1805 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 156; AT: Reduction because NTC over thermal limit on border
20250525 | May | 630 |  | 7718 | 695 |  | 7713 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 5 | 0 | 5 | 1805 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 156; AT: Reduction because NTC over thermal limit on border
20250525 | May | 730 |  | 8443 | 774 |  | 8395 | 774 | -1909 | -1909 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 48 | 0 | 48 | 1909 | 1 | AT: 393; AT: 160
20250525 | May | 830 |  | 8443 | 774 |  | 8395 | 774 | -1909 | -1909 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 48 | 0 | 48 | 1909 | 1 | AT: 393; AT: 160
20250525 | May | 930 | 7762 |  |  | 7761 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 393; AT: 160
20250525 | May | 1030 | 7762 |  |  | 7761 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250525 | May | 1130 | 7762 |  |  | 7761 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250525 | May | 1230 | 8149 |  |  | 8148 |  |  | -1972 | -1972 | -1971 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 414; AT: 160
20250525 | May | 1330 | 8149 |  |  | 8148 |  |  | -1972 | -1972 | -1971 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250525 | May | 1430 | 8149 |  |  | 8148 |  |  | -1972 | -1972 | -1971 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250525 | May | 1530 | 8620 |  |  | 8594 |  |  | -3090 | -3090 | -3065 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250525 | May | 1630 | 8620 |  |  | 8594 |  |  | -3090 | -3090 | -3065 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | AT: 336; AT: 160
20250525 | May | 1730 | 8620 |  |  | 8224 |  |  | -3090 | -3090 | -2695 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 396 | NA | NA | NA | 0 | 1 | AT: 336; AT: 160
20250525 | May | 1830 |  | 6281 | 566 |  | 6281 | 566 | -661 | -661 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 661 | 1 | AT: 336; AT: 160
20250525 | May | 1930 |  | 6281 | 566 |  | 6281 | 566 | -661 | -661 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 661 | 1 | AT: 328; AT: 160
20250525 | May | 2030 |  | 6281 | 566 |  | 6281 | 566 | -661 | -661 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 661 | 1 | AT: 328; AT: 160
20250525 | May | 2130 |  | 6156 | 554 |  | 6155 | 554 | -164 | -164 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 164 | 1 | AT: 330; AT: 160
20250525 | May | 2230 |  | 6156 | 554 |  | 6155 | 554 | -164 | -164 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 164 | 0
20250525 | May | 2330 |  | 6161 | 554 |  | 6161 | 554 | -168 | -168 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 168 | 0
20250526 | May | 30 | 6080 |  |  | 6080 |  |  | -90 | -90 | -90 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 130 | 6080 |  |  | 6080 |  |  | -90 | -90 | -90 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 230 | 6080 |  |  | 6080 |  |  | -90 | -90 | -90 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 330 | 6080 |  |  | 6080 |  |  | -117 | -117 | -117 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 430 | 6080 |  |  | 6080 |  |  | -117 | -117 | -117 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 530 | 6080 |  |  | 6080 |  |  | -117 | -117 | -117 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 630 | 5880 |  |  | 5880 |  |  | -60 | -60 | -60 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 730 | 5630 |  |  | 5630 |  |  | 3569 | 0 | 3569 | TTC Selection - LTTC | TTC Selection - LTTC | 3569 | 0 | NA | NA | NA | 3569 | 0
20250526 | May | 830 | 5630 |  |  | 5630 |  |  | 3569 | 0 | 3569 | TTC Selection - LTTC | TTC Selection - LTTC | 3569 | 0 | NA | NA | NA | 3569 | 0
20250526 | May | 930 | 5630 |  |  | 5630 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 1030 | 5630 |  |  | 5630 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 1130 | 5630 |  |  | 5630 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250526 | May | 1230 | 5789 |  |  | 5783 |  |  | 2449 | 159 | 2296 | Minimum Margin | Validation phase | 2290 | 6 | NA | NA | NA | 4433 | 1 | CH: 5533; CH: Reduction due to missing redispatch potential
20250526 | May | 1330 | 5789 |  |  | 5783 |  |  | 2449 | 159 | 2296 | Minimum Margin | Validation phase | 2290 | 6 | NA | NA | NA | 4433 | 1 | CH: 5533; CH: Reduction due to missing redispatch potential; FR: 2701; FR: Process fail during TSO validation phase
20250526 | May | 1430 | 5799 |  |  | 5793 |  |  | 2449 | 169 | 2286 | Minimum Margin | Validation phase | 2280 | 6 | NA | NA | NA | 4403 | 1 | CH: 5543; CH: Reduction due to missing redispatch potential; FR: 2701; FR: Process fail during TSO validation phase
20250526 | May | 1530 |  | 5370 | 340 |  | 5283 | 340 | 728 | 152 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 576 | NA | 87 | 0 | 87 | -152 | 1 | FR: 2701; FR: Process fail during TSO validation phase
20250526 | May | 1630 |  | 5392 | 342 |  | 5293 | 342 | 728 | 174 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 554 | NA | 99 | 0 | 99 | -174 | 0
20250526 | May | 1730 |  | 5304 | 334 |  | 5255 | 334 | 728 | 86 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 642 | NA | 49 | 0 | 49 | -86 | 0
20250526 | May | 1830 | 5984 |  |  | 5973 |  |  | 1780 | 204 | 1587 | Minimum Margin | Validation phase | 1576 | 11 | NA | NA | NA | 2970 | 1 | CH: 5723; CH: Reduction due to missing redispatch potential
20250526 | May | 1930 | 5780 |  |  | 5780 |  |  | 1780 | 0 | 1780 | TTC Selection - LTTC | TTC Selection - LTTC | 1780 | 0 | NA | NA | NA | 1780 | 0
20250526 | May | 2030 | 5832 |  |  | 5829 |  |  | 1780 | 52 | 1731 | Minimum Margin | Validation phase | 1728 | 3 | NA | NA | NA | 3410 | 1 | CH: 5579; CH: Reduction due to missing redispatch potential
20250526 | May | 2130 |  | 5495 | 441 |  | 5495 | 441 | 2513 | 129 | 0 | Minimum Margin | Minimum Margin | 2384 | NA | 0 | 0 | 0 | -129 | 0
20250526 | May | 2230 |  | 5532 | 444 |  | 5532 | 444 | 2513 | 167 | 0 | Minimum Margin | Minimum Margin | 2346 | NA | 0 | 0 | 0 | -167 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250526 | May | 2330 |  | 5191 | 471 |  | 5190 | 471 | 2875 | 185 | 0 | Minimum Margin | Minimum Margin | 2690 | NA | 1 | 0 | 1 | -185 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250527 | May | 30 | 7581 |  |  | 7579 |  |  | 1426 | 139 | 1288 | Minimum Margin | TTC Validation phase - bilateral reduction | 1287 | 2 | NA | NA | NA | 2437 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250527 | May | 130 | 7778 |  |  | 7631 |  |  | 1426 | 336 | 1235 | Minimum Margin | Validation phase | 1090 | 147 | NA | NA | NA | 2134 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250527 | May | 230 | 7630 |  |  | 7625 |  |  | 1426 | 188 | 1241 | Minimum Margin | TTC Validation phase - bilateral reduction | 1238 | 5 | NA | NA | NA | 2294 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250527 | May | 330 | 8057 |  |  | 8027 |  |  | -1992 | -1992 | -1961 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250527 | May | 430 | 8057 |  |  | 8027 |  |  | -1992 | -1992 | -1961 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250527 | May | 530 | 8057 |  |  | 8027 |  |  | -1992 | -1992 | -1961 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140
20250527 | May | 630 | 7857 |  |  | 7826 |  |  | -1764 | -1764 | -1731 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 416; AT: 140
20250527 | May | 730 | 7646 |  |  | 7509 |  |  | 1046 | 0 | 1183 | Critical Branch | Validation phase | 1046 | 137 | NA | NA | NA | 2366 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250527 | May | 830 | 7647 |  |  | 7509 |  |  | 1046 | 1 | 1183 | Minimum Margin | Validation phase | 1045 | 138 | NA | NA | NA | 2365 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250527 | May | 930 | 8566 |  |  | 8016 |  |  | -1489 | -1489 | -937 | Critical Branch | Validation phase | 0 | 550 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250527 | May | 1030 | 8566 |  |  | 8016 |  |  | -1489 | -1489 | -937 | Critical Branch | Validation phase | 0 | 550 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250527 | May | 1130 | 8566 |  |  | 8016 |  |  | -1489 | -1489 | -937 | Critical Branch | Validation phase | 0 | 550 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250527 | May | 1230 | 7757 |  |  | 7757 |  |  | -1659 | -1659 | -1658 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250527 | May | 1330 | 7757 |  |  | 7757 |  |  | -1659 | -1659 | -1658 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 364; AT: 140
20250527 | May | 1430 | 7757 |  |  | 7757 |  |  | -1659 | -1659 | -1658 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 364; AT: 140
20250527 | May | 1530 | 6759 |  |  | 6759 |  |  | 1722 | 2 | 1720 | Minimum Margin | TTC Validation phase - bilateral reduction | 1720 | 0 | NA | NA | NA | 3438 | 1 | AT: 370; AT: 140
20250527 | May | 1630 | 6759 |  |  | 6759 |  |  | 1722 | 2 | 1720 | Minimum Margin | TTC Validation phase - bilateral reduction | 1720 | 0 | NA | NA | NA | 3438 | 1 | AT: 411; AT: 140
20250527 | May | 1730 | 6870 |  |  | 6863 |  |  | 1722 | 113 | 1615 | Minimum Margin | Validation phase | 1609 | 7 | NA | NA | NA | 3117 | 1 | AT: 411; AT: 140
20250527 | May | 1830 |  | 7166 | 642 |  | 7165 | 642 | -734 | -734 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 734 | 1 | AT: 411; AT: 140
20250527 | May | 1930 |  | 7166 | 642 |  | 7165 | 642 | -734 | -734 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 734 | 1 | AT: 381; AT: 140
20250527 | May | 2030 |  | 7166 | 642 |  | 7165 | 642 | -734 | -734 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 734 | 1 | AT: 375; AT: 140
20250527 | May | 2130 |  | 6667 | 597 |  | 6667 | 597 | 984 | 126 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 858 | NA | 0 | 0 | 0 | -126 | 1 | AT: 362; AT: 160
20250527 | May | 2230 |  | 6568 | 588 |  | 6568 | 588 | 984 | 27 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 957 | NA | 0 | 0 | 0 | -27 | 0
20250527 | May | 2330 |  | 6196 | 612 |  | 6195 | 612 | 1398 | 15 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1383 | NA | 1 | 0 | 1 | -15 | 0
20250528 | May | 30 | 6201 |  |  | 6201 |  |  | -1056 | -1056 | -1056 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 130 | 6201 |  |  | 6201 |  |  | -1056 | -1056 | -1056 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 230 | 6201 |  |  | 6201 |  |  | -1056 | -1056 | -1056 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 330 | 6687 |  |  | 6687 |  |  | -930 | -930 | -930 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 430 | 6687 |  |  | 6687 |  |  | -930 | -930 | -930 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 530 | 6687 |  |  | 6687 |  |  | -930 | -930 | -930 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 630 | 6487 |  |  | 6487 |  |  | -696 | -696 | -696 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 730 | 6061 |  |  | 6061 |  |  | -938 | -938 | -938 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 830 | 6061 |  |  | 6061 |  |  | -938 | -938 | -938 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 930 | 5630 |  |  | 5630 |  |  | -1409 | -1409 | -1409 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1030 | 5630 |  |  | 5630 |  |  | -1409 | -1409 | -1409 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1130 | 5630 |  |  | 5630 |  |  | -1409 | -1409 | -1409 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1230 | 5630 |  |  | 5630 |  |  | -3053 | -3053 | -3053 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1330 | 5630 |  |  | 5630 |  |  | -3053 | -3053 | -3053 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1430 | 5630 |  |  | 5630 |  |  | -3053 | -3053 | -3053 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1530 | 5630 |  |  | 5630 |  |  | -3321 | -3321 | -3321 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1630 | 5630 |  |  | 5630 |  |  | -3321 | -3321 | -3321 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1730 | 5630 |  |  | 5630 |  |  | -3321 | -3321 | -3321 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 1830 |  | 6541 | 586 |  | 6541 | 586 | -4059 | -4059 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4059 | 0
20250528 | May | 1930 |  | 6541 | 586 |  | 6541 | 586 | -4059 | -4059 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4059 | 0
20250528 | May | 2030 |  | 6541 | 586 |  | 6541 | 586 | -4059 | -4059 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4059 | 0
20250528 | May | 2130 | 6385 |  |  | 6385 |  |  | -2531 | -2531 | -2531 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250528 | May | 2230 | 6385 |  |  | 6385 |  |  | -2531 | -2531 | -2531 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250528 | May | 2330 | 5985 |  |  | 5985 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 30 | 8165 |  |  | 7316 |  |  | -2243 | -2243 | -1394 | Critical Branch | Validation phase | 0 | 849 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 130 | 8165 |  |  | 7316 |  |  | -2243 | -2243 | -1394 | Critical Branch | Validation phase | 0 | 849 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 230 | 8165 |  |  | 7316 |  |  | -2243 | -2243 | -1394 | Critical Branch | Validation phase | 0 | 849 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 330 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 430 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 530 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250529 | May | 630 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250529 | May | 730 | 7950 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250529 | May | 830 | 7950 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250529 | May | 930 | 7897 |  |  | 6552 |  |  | -1973 | -1973 | -628 | Critical Branch | Validation phase | 0 | 1345 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250529 | May | 1030 | 7897 |  |  | 6552 |  |  | -1973 | -1973 | -628 | Critical Branch | Validation phase | 0 | 1345 | NA | NA | NA | 0 | 1 | AT: 375; AT: 140
20250529 | May | 1130 | 7897 |  |  | 6552 |  |  | -1973 | -1973 | -628 | Critical Branch | Validation phase | 0 | 1345 | NA | NA | NA | 0 | 1 | AT: 375; AT: 140
20250529 | May | 1230 | 7078 |  |  | 6145 |  |  | -1297 | -1297 | -364 | Critical Branch | Validation phase | 0 | 933 | NA | NA | NA | 0 | 1 | AT: 375; AT: 140
20250529 | May | 1330 | 7078 |  |  | 6145 |  |  | -1297 | -1297 | -364 | Critical Branch | Validation phase | 0 | 933 | NA | NA | NA | 0 | 1 | AT: 327; AT: 140
20250529 | May | 1430 | 7078 |  |  | 6145 |  |  | -1297 | -1297 | -364 | Critical Branch | Validation phase | 0 | 933 | NA | NA | NA | 0 | 1 | AT: 331; AT: 140
20250529 | May | 1530 |  | 5791 | 523 |  | 5791 | 523 | -735 | -735 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 735 | 1 | AT: 331; AT: 140
20250529 | May | 1630 |  | 6091 | 523 |  | 6091 | 523 | -1057 | -1057 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1057 | 1 | AT: 312; AT: 140
20250529 | May | 1730 |  | 6091 | 523 |  | 6091 | 523 | -1057 | -1057 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1057 | 1 | AT: 312; AT: 140
20250529 | May | 1830 |  | 5778 | 496 |  | 5777 | 496 | -2205 | -2205 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2205 | 1 | AT: 312; AT: 140
20250529 | May | 1930 |  | 5778 | 496 |  | 5777 | 496 | -2205 | -2205 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2205 | 1 | AT: 308; AT: 140
20250529 | May | 2030 |  | 5778 | 496 |  | 5777 | 496 | -2205 | -2205 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2205 | 1 | AT: 308; AT: 140
20250529 | May | 2130 | 6129 |  |  | 6128 |  |  | -1623 | -1623 | -1623 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 295; AT: 160
20250529 | May | 2230 | 6129 |  |  | 6128 |  |  | -1623 | -1623 | -1623 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250529 | May | 2330 | 5729 |  |  | 5729 |  |  | -1225 | -1225 | -1225 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250530 | May | 30 | 8621 |  |  | 8467 |  |  | -1374 | -1374 | -1233 | Critical Branch | Validation phase | 0 | 154 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250530 | May | 130 | 8621 |  |  | 8467 |  |  | -1374 | -1374 | -1233 | Critical Branch | Validation phase | 0 | 154 | NA | NA | NA | 0 | 1 | AT: 359; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250530 | May | 230 | 8621 |  |  | 8467 |  |  | -1374 | -1374 | -1233 | Critical Branch | Validation phase | 0 | 154 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250530 | May | 330 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | 0 | 125 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250530 | May | 430 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | 0 | 125 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250530 | May | 530 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | 0 | 125 | NA | NA | NA | 0 | 1 | AT: 407; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250530 | May | 630 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | 0 | 125 | NA | NA | NA | 0 | 1 | AT: 379; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250530 | May | 730 | 7925 |  |  | 7925 |  |  | -206 | -206 | -206 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 310; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250530 | May | 830 | 7925 |  |  | 7661 |  |  | -206 | -206 | 52 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 264 | NA | NA | NA | 310 | 1 | AT: 255; AT: Reduction because NTC over thermal limit on border; AT: -255; AT: Reduction because NTC over thermal limit on border
20250530 | May | 930 | 6167 |  |  | 6161 |  |  | 2131 | 87 | 2051 | Minimum Margin | Validation phase | 2044 | 6 | NA | NA | NA | 4015 | 1 | AT: 315; AT: Reduction because NTC over thermal limit on border; AT: -315; AT: Reduction because NTC over thermal limit on border
20250530 | May | 1030 | 6297 |  |  | 6250 |  |  | 2131 | 217 | 1961 | Minimum Margin | Validation phase | 1914 | 47 | NA | NA | NA | 3705 | 1 | AT: 313; AT: Reduction because NTC over thermal limit on border; AT: -313; AT: Reduction because NTC over thermal limit on border
20250530 | May | 1130 | 6293 |  |  | 6250 |  |  | 2131 | 213 | 1961 | Minimum Margin | Validation phase | 1918 | 43 | NA | NA | NA | 3709 | 1 | AT: 315; AT: Reduction because NTC over thermal limit on border; AT: -315; AT: Reduction because NTC over thermal limit on border
20250530 | May | 1230 | 6232 |  |  | 6221 |  |  | 2621 | 152 | 2480 | Minimum Margin | Validation phase | 2469 | 11 | NA | NA | NA | 4808 | 1 | AT: 314; AT: Reduction because NTC over thermal limit on border; AT: -314; AT: Reduction because NTC over thermal limit on border
20250530 | May | 1330 | 6263 |  |  | 6249 |  |  | 2621 | 183 | 2452 | Minimum Margin | Validation phase | 2438 | 14 | NA | NA | NA | 4721 | 1 | AT: 316; AT: Reduction because NTC over thermal limit on border; AT: -316; AT: Reduction because NTC over thermal limit on border; FR: 2767; FR: Process fail during TSO validation phase
20250530 | May | 1430 | 6246 |  |  | 6234 |  |  | 2621 | 166 | 2467 | Minimum Margin | Validation phase | 2455 | 12 | NA | NA | NA | 4768 | 1 | AT: 313; AT: Reduction because NTC over thermal limit on border; AT: -313; AT: Reduction because NTC over thermal limit on border; FR: 2767; FR: Process fail during TSO validation phase
20250530 | May | 1530 |  | 5835 | 387 |  | 5741 | 387 | 1967 | 174 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1793 | NA | 94 | 0 | 94 | -174 | 1 | AT: 315; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 2767; FR: Process fail during TSO validation phase
20250530 | May | 1630 |  | 5790 | 383 |  | 5720 | 383 | 1967 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1838 | NA | 70 | 0 | 70 | -129 | 1 | AT: 104; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border; FR: 3329; FR: Process fail during TSO validation phase
20250530 | May | 1730 |  | 5830 | 386 |  | 5738 | 386 | 1967 | 169 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1798 | NA | 92 | 0 | 92 | -169 | 1 | AT: 379; AT: 140; FR: 3329; FR: Process fail during TSO validation phase
20250530 | May | 1830 |  | 6753 | 580 |  | 6732 | 580 | 2195 | 37 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2158 | NA | 21 | 0 | 21 | -37 | 1 | AT: 379; AT: 140; FR: 3329; FR: Process fail during TSO validation phase
20250530 | May | 1930 |  | 6909 | 594 |  | 6805 | 594 | 2195 | 193 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2002 | NA | 104 | 0 | 104 | -193 | 1 | AT: 368; AT: 140
20250530 | May | 2030 |  | 6901 | 593 |  | 6802 | 593 | 2195 | 185 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2010 | NA | 99 | 0 | 99 | -185 | 1 | AT: 368; AT: 140
20250530 | May | 2130 | 7214 |  |  | 7214 |  |  | -1554 | -1554 | -1554 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 356; AT: 160
20250530 | May | 2230 | 7214 |  |  | 7214 |  |  | -1554 | -1554 | -1554 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 328; AT: 160
20250530 | May | 2330 | 6814 |  |  | 6813 |  |  | -1157 | -1157 | -1157 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 328; AT: 160
20250531 | May | 30 | 6313 |  |  | 6313 |  |  | -703 | -703 | -703 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 328; AT: 160
20250531 | May | 130 | 6313 |  |  | 6313 |  |  | -703 | -703 | -703 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 317; AT: 160
20250531 | May | 230 | 6313 |  |  | 6313 |  |  | -703 | -703 | -703 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 319; AT: 160
20250531 | May | 330 | 6129 |  |  | 6128 |  |  | 26 | 0 | 27 | Critical Branch | TTC Validation phase - bilateral reduction | 26 | 1 | NA | NA | NA | 54 | 1 | AT: 319; AT: 160
20250531 | May | 430 | 6155 |  |  | 6155 |  |  | 26 | 26 | 0 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | -26 | 1 | AT: 317; AT: 160
20250531 | May | 530 | 6155 |  |  | 6155 |  |  | 26 | 26 | 0 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | -26 | 1 | AT: 310; AT: 140
20250531 | May | 630 | 6130 |  |  | 6129 |  |  | 26 | 1 | 26 | Minimum Margin | TTC Validation phase - bilateral reduction | 25 | 1 | NA | NA | NA | 26 | 1 | AT: 310; AT: 140
20250531 | May | 730 | 6154 |  |  | 6154 |  |  | -333 | -333 | -333 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 140
20250531 | May | 830 | 6154 |  |  | 6154 |  |  | -333 | -333 | -333 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250531 | May | 930 | 8306 |  |  | 7654 |  |  | -1848 | -1848 | -1197 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 652 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250531 | May | 1030 | 8306 |  |  | 8229 |  |  | -1848 | -1848 | -1771 | Critical Branch | Validation phase | 0 | 77 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140
20250531 | May | 1130 | 8306 |  |  | 8229 |  |  | -1848 | -1848 | -1771 | Critical Branch | Validation phase | 0 | 77 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140
20250531 | May | 1230 | 7230 |  |  | 7230 |  |  | -1287 | -1287 | -1287 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 369; AT: 140
20250531 | May | 1330 | 7230 |  |  | 7230 |  |  | -1287 | -1287 | -1287 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 328; AT: 140
20250531 | May | 1430 | 7230 |  |  | 7230 |  |  | -1287 | -1287 | -1287 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 328; AT: 140
20250531 | May | 1530 | 6483 |  |  | 6483 |  |  | -694 | -694 | -694 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 328; AT: 140
20250531 | May | 1630 | 6483 |  |  | 6483 |  |  | -694 | -694 | -694 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 353; AT: 140; FR: 3196; FR: Process fail during TSO validation phase
20250531 | May | 1730 | 6483 |  |  | 6483 |  |  | -694 | -694 | -694 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 353; AT: 140; FR: 3196; FR: Process fail during TSO validation phase
20250531 | May | 1830 |  | 6468 | 555 |  | 6466 | 555 | 2276 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2274 | NA | 2 | 0 | 2 | -2 | 1 | AT: 353; AT: 140; FR: 3196; FR: Process fail during TSO validation phase
20250531 | May | 1930 |  | 6468 | 555 |  | 6466 | 555 | 2276 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2274 | NA | 2 | 0 | 2 | -2 | 1 | AT: 306; AT: 140
20250531 | May | 2030 |  | 6468 | 555 |  | 6466 | 555 | 2276 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 2274 | NA | 2 | 0 | 2 | -2 | 1 | AT: 306; AT: 140
20250531 | May | 2130 | 6080 |  |  | 6080 |  |  | -1278 | -1278 | -1278 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 292; AT: 160
20250531 | May | 2230 | 6080 |  |  | 6080 |  |  | -1278 | -1278 | -1278 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250531 | May | 2330 | 5680 |  |  | 5680 |  |  | -883 | -883 | -883 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250601 | June | 30 | 8165 |  |  | 8147 |  |  | -1440 | -1440 | -1429 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250601 | June | 130 | 8165 |  |  | 8147 |  |  | -1440 | -1440 | -1429 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20250601 | June | 230 | 8165 |  |  | 8147 |  |  | -1440 | -1440 | -1429 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 18 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20250601 | June | 330 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 78 | 0 | 78 | 2444 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20250601 | June | 430 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 78 | 0 | 78 | 2444 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 151; AT: Reduction because NTC over thermal limit on border
20250601 | June | 530 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 78 | 0 | 78 | 2444 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250601 | June | 630 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 78 | 0 | 78 | 2444 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250601 | June | 730 |  | 7564 | 975 |  | 7564 | 954 | 385 | 323 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 62 | NA | 0 | 21 | 21 | -323 | 1 | AT: 343; AT: 160
20250601 | June | 830 |  | 7613 | 981 |  | 7034 | 959 | 385 | 372 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 13 | NA | 579 | 22 | 601 | -372 | 1 | AT: 343; AT: 160
20250601 | June | 930 | 6495 |  |  | 6495 |  |  | -319 | -319 | -319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 343; AT: 160
20250601 | June | 1030 | 6495 |  |  | 6495 |  |  | -319 | -319 | -319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 160
20250601 | June | 1130 | 6495 |  |  | 6495 |  |  | -319 | -319 | -319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 160
20250601 | June | 1230 | 7340 |  |  | 7340 |  |  | -801 | -801 | -801 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 392; AT: 160
20250601 | June | 1330 | 7340 |  |  | 7340 |  |  | -801 | -801 | -801 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250601 | June | 1430 | 7340 |  |  | 7340 |  |  | -801 | -801 | -801 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250601 | June | 1530 | 6965 |  |  | 6964 |  |  | -520 | -520 | -520 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 370; AT: 160
20250601 | June | 1630 | 6965 |  |  | 6964 |  |  | -520 | -520 | -520 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250601 | June | 1730 | 6965 |  |  | 6964 |  |  | -520 | -520 | -520 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250601 | June | 1830 |  | 7588 | 735 |  | 7564 | 735 | -322 | -322 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 24 | 0 | 24 | 322 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250601 | June | 1930 |  | 7588 | 735 |  | 7564 | 735 | -322 | -322 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 24 | 0 | 24 | 322 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250601 | June | 2030 |  | 7588 | 735 |  | 7564 | 735 | -322 | -322 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 24 | 0 | 24 | 322 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250601 | June | 2130 |  | 7931 | 778 |  | 7885 | 778 | -2590 | -2590 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 46 | 0 | 46 | 2590 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250601 | June | 2230 |  | 7931 | 778 |  | 7885 | 778 | -2590 | -2590 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 46 | 0 | 46 | 2590 | 1 | AT: 231; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 4325; FR: Process fail during TSO validation phase
20250601 | June | 2330 |  | 8138 | 778 |  | 8088 | 778 | -2704 | -2704 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 50 | 0 | 50 | 2704 | 1 | AT: 231; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 4325; FR: Process fail during TSO validation phase
20250602 | June | 30 |  | 8205 | 1031 |  | 8168 | 998 | 395 | 64 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 331 | NA | 37 | 33 | 70 | -64 | 1 | AT: 231; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 4325; FR: Process fail during TSO validation phase
20250602 | June | 130 |  | 8205 | 1031 |  | 8168 | 998 | 395 | 64 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 331 | NA | 37 | 33 | 70 | -64 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250602 | June | 230 |  | 8205 | 1031 |  | 8168 | 998 | 395 | 64 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 331 | NA | 37 | 33 | 70 | -64 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250602 | June | 330 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1232 | NA | 6 | 0 | 6 | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250602 | June | 430 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1232 | NA | 6 | 0 | 6 | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250602 | June | 530 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1232 | NA | 6 | 0 | 6 | 0 | 1 | AT: 193; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 630 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1232 | NA | 6 | 0 | 6 | 0 | 1 | AT: 192; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 730 |  | 6882 | 883 |  | 6882 | 880 | -2915 | -2915 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 3 | 3 | 2915 | 1 | AT: 298; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 830 |  | 6882 | 883 |  | 6821 | 880 | -2915 | -2915 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 61 | 3 | 64 | 2915 | 1 | AT: 298; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 930 | 5815 |  |  | 5804 |  |  | 4529 | 135 | 4405 | Minimum Margin | Validation phase | 4394 | 11 | NA | NA | NA | 8675 | 1 | AT: 299; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1030 | 5815 |  |  | 5804 |  |  | 4529 | 135 | 4405 | Minimum Margin | Validation phase | 4394 | 11 | NA | NA | NA | 8675 | 1 | AT: 385; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1130 | 5823 |  |  | 5811 |  |  | 4529 | 143 | 4398 | Minimum Margin | Validation phase | 4386 | 12 | NA | NA | NA | 8653 | 1 | AT: 414; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1230 | 7845 |  |  | 7311 |  |  | -1800 | -1800 | -1280 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 534 | NA | NA | NA | 0 | 1 | AT: 377; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1330 | 7845 |  |  | 7844 |  |  | -1800 | -1800 | -1799 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 291; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1430 | 7845 |  |  | 7180 |  |  | -1800 | -1800 | -1152 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 665 | NA | NA | NA | 0 | 1 | AT: 291; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1530 | 5680 |  |  | 5680 |  |  | -1382 | -1382 | -1382 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 291; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1630 | 5680 |  |  | 5680 |  |  | -1382 | -1382 | -1382 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 379; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1730 | 5680 |  |  | 5680 |  |  | -1382 | -1382 | -1382 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 382; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1830 |  | 6793 | 639 |  | 6741 | 639 | 3875 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 3875 | NA | 52 | 0 | 52 | 0 | 1 | AT: 382; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250602 | June | 1930 |  | 6793 | 639 |  | 6792 | 639 | 3875 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 3875 | NA | 1 | 0 | 1 | 0 | 1 | AT: 366; AT: 108
20250602 | June | 2030 |  | 6793 | 639 |  | 6792 | 639 | 3875 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 3875 | NA | 1 | 0 | 1 | 0 | 1 | AT: 366; AT: 108
20250602 | June | 2130 |  | 4979 | 609 |  | 4979 | 608 | -2179 | -2179 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 2179 | 1 | AT: 367; AT: 108
20250602 | June | 2230 |  | 4979 | 609 |  | 4979 | 608 | -2179 | -2179 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 2179 | 0
20250602 | June | 2330 |  | 4979 | 609 |  | 4979 | 608 | -2179 | -2179 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 1 | 1 | 2179 | 0
20250603 | June | 30 |  | 6231 | 586 |  | 6231 | 586 | -2087 | -2087 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2087 | 0
20250603 | June | 130 |  | 6231 | 586 |  | 6231 | 586 | -2087 | -2087 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2087 | 0
20250603 | June | 230 |  | 6231 | 586 |  | 6231 | 586 | -2087 | -2087 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2087 | 0
20250603 | June | 330 |  | 6418 | 603 |  | 6418 | 603 | -1798 | -1798 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1798 | 0
20250603 | June | 430 |  | 6418 | 603 |  | 6418 | 603 | -1798 | -1798 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1798 | 0
20250603 | June | 530 |  | 6418 | 603 |  | 6418 | 603 | -1798 | -1798 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1798 | 0
20250603 | June | 630 |  | 6218 | 603 |  | 6218 | 603 | -1590 | -1590 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 1590 | 0
20250603 | June | 730 |  | 6028 | 532 |  | 6028 | 532 | -2230 | -2230 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2230 | 0
20250603 | June | 830 |  | 6028 | 532 |  | 6028 | 532 | -2230 | -2230 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2230 | 0
20250603 | June | 930 | 6455 |  |  | 6455 |  |  | 2421 | 0 | 2421 | Critical Branch | Critical Branch | 2421 | 0 | NA | NA | NA | 2421 | 0
20250603 | June | 1030 | 6585 |  |  | 6582 |  |  | 2421 | 130 | 2294 | Minimum Margin | Validation phase | 2291 | 3 | NA | NA | NA | 4458 | 1 | CH: 6332; CH: Reduction due to missing redispatch potential
20250603 | June | 1130 | 6654 |  |  | 6651 |  |  | 2421 | 199 | 2225 | Minimum Margin | Validation phase | 2222 | 3 | NA | NA | NA | 4251 | 1 | CH: 6401; CH: Reduction due to missing redispatch potential
20250603 | June | 1230 | 7145 |  |  | 7139 |  |  | 2804 | 170 | 2640 | Minimum Margin | Validation phase | 2634 | 6 | NA | NA | NA | 5110 | 1 | CH: 6889; CH: Reduction due to missing redispatch potential
20250603 | June | 1330 | 7145 |  |  | 7139 |  |  | 2804 | 170 | 2640 | Minimum Margin | Validation phase | 2634 | 6 | NA | NA | NA | 5110 | 1 | CH: 6889; CH: Reduction due to missing redispatch potential
20250603 | June | 1430 | 7145 |  |  | 7139 |  |  | 2804 | 170 | 2640 | Minimum Margin | Validation phase | 2634 | 6 | NA | NA | NA | 5110 | 1 | CH: 6889; CH: Reduction due to missing redispatch potential
20250603 | June | 1530 | 6541 |  |  | 6539 |  |  | 2258 | 189 | 2071 | Minimum Margin | Validation phase | 2069 | 2 | NA | NA | NA | 3953 | 1 | CH: 6289; CH: Reduction due to missing redispatch potential
20250603 | June | 1630 | 6554 |  |  | 6548 |  |  | 2258 | 202 | 2062 | Minimum Margin | Validation phase | 2056 | 6 | NA | NA | NA | 3922 | 1 | CH: 6302; CH: Reduction due to missing redispatch potential
20250603 | June | 1730 | 6352 |  |  | 6352 |  |  | 2258 | 0 | 2258 | Critical Branch | Critical Branch | 2258 | 0 | NA | NA | NA | 2258 | 0
20250603 | June | 1830 |  | 5661 | 475 |  | 5661 | 475 | -2479 | -2479 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2479 | 0
20250603 | June | 1930 |  | 5661 | 475 |  | 5661 | 475 | -2479 | -2479 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2479 | 0
20250603 | June | 2030 |  | 5661 | 475 |  | 5661 | 475 | -2479 | -2479 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2479 | 0
20250603 | June | 2130 |  | 5966 | 512 |  | 5966 | 512 | -2543 | -2543 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2543 | 0
20250603 | June | 2230 |  | 5966 | 512 |  | 5966 | 512 | -2543 | -2543 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2543 | 0
20250603 | June | 2330 |  | 5606 | 537 |  | 5606 | 537 | -2140 | -2140 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 2140 | 0
20250604 | June | 30 | 5780 |  |  | 5780 |  |  | -1055 | -1055 | -1055 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250604 | June | 130 | 5780 |  |  | 5780 |  |  | -1055 | -1055 | -1055 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250604 | June | 230 | 5780 |  |  | 5780 |  |  | -1055 | -1055 | -1055 | TTC Selection - LTTC | TTC Selection - LTTC | 0 | 0 | NA | NA | NA | 0 | 0
20250604 | June | 330 | 6760 |  |  | 6760 |  |  | -1112 | -1112 | -1112 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250604 | June | 430 | 6760 |  |  | 6760 |  |  | -1112 | -1112 | -1112 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250604 | June | 530 | 6760 |  |  | 6760 |  |  | -1112 | -1112 | -1112 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 630 | 6560 |  |  | 6485 |  |  | -891 | -891 | -817 | Critical Branch | Smoothing ramp | 0 | 75 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 730 | 5617 |  |  | 4985 |  |  | -1119 | -1119 | -493 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 632 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 830 | 5617 |  |  | 4985 |  |  | -1119 | -1119 | -493 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 632 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 930 | 5232 |  |  | 4776 |  |  | 3701 | 2 | 4660 | Minimum Margin | TTC Validation phase - bilateral reduction | 3699 | 456 | NA | NA | NA | 9318 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1030 | 5463 |  |  | 4895 |  |  | 3701 | 233 | 4652 | Minimum Margin | Validation phase | 3468 | 568 | NA | NA | NA | 9071 | 1 | CH: 5201; CH: Reduction due to missing redispatch potential; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1130 | 5232 |  |  | 4776 |  |  | 3701 | 2 | 4660 | Minimum Margin | TTC Validation phase - bilateral reduction | 3699 | 456 | NA | NA | NA | 9318 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1230 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1444 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1330 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1444 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1430 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1444 | NA | NA | NA | 0 | 1 | FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1530 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1444 | NA | NA | NA | 0 | 0
20250604 | June | 1630 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1444 | NA | NA | NA | 0 | 0
20250604 | June | 1730 | 8100 |  |  | 7456 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 644 | NA | NA | NA | 0 | 1
20250604 | June | 1830 |  | 5661 | 421 |  | 5661 | 421 | -2440 | -2440 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2440 | 0
20250604 | June | 1930 |  | 5661 | 421 |  | 5661 | 421 | -2440 | -2440 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2440 | 0
20250604 | June | 2030 |  | 5661 | 421 |  | 5661 | 421 | -2440 | -2440 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2440 | 0
20250604 | June | 2130 |  | 5661 | 389 |  | 5661 | 389 | -3204 | -3204 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 3204 | 0
20250604 | June | 2230 |  | 5661 | 389 |  | 5661 | 389 | -3204 | -3204 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 3204 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3931; FR: Cancellation planned outage Chaffard G.Ile 2
20250604 | June | 2330 |  | 5301 | 414 |  | 5301 | 414 | -2807 | -2807 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 2807 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3931; FR: Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 30 | 8739 |  |  | 6300 |  |  | -3107 | -3107 | -915 | Critical Branch | Validation phase | 0 | 2439 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3931; FR: Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 130 | 8739 |  |  | 6300 |  |  | -3107 | -3107 | -915 | Critical Branch | Validation phase | 0 | 2439 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3822; FR: Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 230 | 8739 |  |  | 6300 |  |  | -3107 | -3107 | -915 | Critical Branch | Validation phase | 0 | 2439 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3822; FR: Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 330 | 8517 |  |  | 6223 |  |  | -2580 | -2580 | -531 | Critical Branch | Validation phase | 0 | 2294 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3822; FR: Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 430 | 8517 |  |  | 6223 |  |  | -2580 | -2580 | -531 | Critical Branch | Validation phase | 0 | 2294 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border; FR: 3822; FR: Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 530 | 8517 |  |  | 6223 |  |  | -2580 | -2580 | -531 | Critical Branch | Validation phase | 0 | 2294 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 630 | 8317 |  |  | 6013 |  |  | -2353 | -2353 | -285 | Critical Branch | Validation phase | 0 | 2304 | NA | NA | NA | 0 | 1 | AT: 384; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 730 | 6960 |  |  | 5716 |  |  | 5101 | 19 | 7663 | Minimum Margin | TTC Validation phase - bilateral reduction | 5082 | 1244 | NA | NA | NA | 15307 | 1 | AT: 292; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 830 | 6958 |  |  | 5702 |  |  | 5101 | 17 | 7667 | Minimum Margin | TTC Validation phase - bilateral reduction | 5084 | 1256 | NA | NA | NA | 15317 | 1 | AT: 305; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 930 | 5245 |  |  | 4783 |  |  | 4149 | 15 | 5103 | Minimum Margin | TTC Validation phase - bilateral reduction | 4134 | 462 | NA | NA | NA | 10191 | 1 | AT: 304; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1030 | 5452 |  |  | 4892 |  |  | 4149 | 222 | 5094 | Minimum Margin | Validation phase | 3927 | 560 | NA | NA | NA | 9966 | 1 | AT: 304; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1130 | 5438 |  |  | 4884 |  |  | 4149 | 208 | 5095 | Minimum Margin | Validation phase | 3941 | 554 | NA | NA | NA | 9982 | 1 | AT: 304; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1230 | 5437 |  |  | 4885 |  |  | 3669 | 207 | 4615 | Minimum Margin | Validation phase | 3462 | 552 | NA | NA | NA | 9023 | 1 | AT: 304; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1330 | 5437 |  |  | 4885 |  |  | 3669 | 207 | 4615 | Minimum Margin | Validation phase | 3462 | 552 | NA | NA | NA | 9023 | 1 | AT: 291; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1430 | 5439 |  |  | 4886 |  |  | 3669 | 209 | 4615 | Minimum Margin | Validation phase | 3460 | 553 | NA | NA | NA | 9021 | 1 | AT: 291; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1530 | 5234 |  |  | 4776 |  |  | 3776 | 4 | 4730 | Minimum Margin | TTC Validation phase - bilateral reduction | 3772 | 458 | NA | NA | NA | 9456 | 1 | AT: 304; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1630 | 5241 |  |  | 4780 |  |  | 3776 | 11 | 4729 | Minimum Margin | TTC Validation phase - bilateral reduction | 3765 | 461 | NA | NA | NA | 9447 | 1 | AT: 334; AT: 140
20250605 | June | 1730 | 5942 |  |  | 4889 |  |  | 2297 | 12 | 4288 | Minimum Margin | TTC Validation phase - bilateral reduction | 2285 | 1053 | NA | NA | NA | 8564 | 1 | AT: 334; AT: 140
20250605 | June | 1830 |  | 6153 | 528 |  | 5924 | 528 | -2650 | -2650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 229 | 0 | 229 | 2650 | 1 | AT: 334; AT: 140
20250605 | June | 1930 |  | 6153 | 528 |  | 6152 | 528 | -2650 | -2650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2650 | 1 | AT: 355; AT: 140
20250605 | June | 2030 |  | 6153 | 528 |  | 6152 | 528 | -2650 | -2650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2650 | 1 | AT: 355; AT: 140
20250605 | June | 2130 | 6983 |  |  | 6982 |  |  | -2595 | -2595 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 343; AT: 160
20250605 | June | 2230 | 6983 |  |  | 6982 |  |  | -2595 | -2595 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250605 | June | 2330 | 6583 |  |  | 6583 |  |  | -2198 | -2198 | -2198 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250606 | June | 30 | 9213 |  |  | 8690 |  |  | -3262 | -3262 | -2736 | Critical Branch | Validation phase | 0 | 523 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250606 | June | 130 | 9213 |  |  | 8690 |  |  | -3262 | -3262 | -2736 | Critical Branch | Validation phase | 0 | 523 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250606 | June | 230 | 9213 |  |  | 8690 |  |  | -3262 | -3262 | -2736 | Critical Branch | Validation phase | 0 | 523 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250606 | June | 330 | 8997 |  |  | 8690 |  |  | -1597 | -1597 | -1311 | Critical Branch | Validation phase | 0 | 307 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250606 | June | 430 | 8997 |  |  | 8690 |  |  | -1597 | -1597 | -1311 | Critical Branch | Validation phase | 0 | 307 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250606 | June | 530 | 8997 |  |  | 8544 |  |  | -1597 | -1597 | -1165 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 453 | NA | NA | NA | 0 | 1 | AT: 378; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 630 | 8797 |  |  | 7044 |  |  | -1467 | -1467 | 265 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1753 | NA | NA | NA | 1997 | 1 | AT: 378; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 730 | 7267 |  |  | 5544 |  |  | 2266 | 0 | 5524 | Critical Branch | TTC Validation phase - bilateral reduction | 2266 | 1723 | NA | NA | NA | 11048 | 1 | AT: 304; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 830 | 7267 |  |  | 5544 |  |  | 2266 | 0 | 5524 | Critical Branch | TTC Validation phase - bilateral reduction | 2266 | 1723 | NA | NA | NA | 11048 | 1 | AT: 307; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 930 | 5953 |  |  | 4894 |  |  | 3218 | 23 | 5211 | Minimum Margin | TTC Validation phase - bilateral reduction | 3195 | 1059 | NA | NA | NA | 10399 | 1 | AT: 303; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1030 | 6002 |  |  | 4918 |  |  | 3218 | 72 | 5209 | Minimum Margin | TTC Validation phase - bilateral reduction | 3146 | 1084 | NA | NA | NA | 10346 | 1 | AT: 351; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1130 | 5930 |  |  | 4883 |  |  | 3218 | 0 | 5212 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 3218 | 1047 | NA | NA | NA | 10424 | 1 | AT: 351; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1230 | 6779 |  |  | 5303 |  |  | -3754 | -3754 | -2351 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1476 | NA | NA | NA | 0 | 1 | AT: 351; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1330 | 6779 |  |  | 5303 |  |  | -3754 | -3754 | -2351 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1476 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1430 | 6779 |  |  | 5303 |  |  | -3754 | -3754 | -2351 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1476 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1530 | 7503 |  |  | 5660 |  |  | -4302 | -4302 | -2553 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1843 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140; FR: 1700; FR: Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1630 | 7503 |  |  | 5660 |  |  | -4302 | -4302 | -2553 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1843 | NA | NA | NA | 0 | 1 | AT: 337; AT: 140
20250606 | June | 1730 | 7503 |  |  | 5660 |  |  | -4302 | -4302 | -2553 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1843 | NA | NA | NA | 0 | 1 | AT: 338; AT: 140
20250606 | June | 1830 |  | 6202 | 532 |  | 6201 | 532 | 4574 | 111 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4463 | NA | 1 | 0 | 1 | -111 | 1 | AT: 331; AT: 140
20250606 | June | 1930 |  | 6205 | 533 |  | 6205 | 533 | 4574 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4460 | NA | 0 | 0 | 0 | -114 | 1 | AT: 413; AT: 139
20250606 | June | 2030 |  | 6093 | 523 |  | 6093 | 523 | 4574 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 4572 | NA | 0 | 0 | 0 | -2 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250606 | June | 2130 |  | 7841 | 673 |  | 7480 | 673 | -1814 | -1814 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 361 | 0 | 361 | 1814 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 159; AT: Reduction because NTC over thermal limit on border
20250606 | June | 2230 |  | 7841 | 673 |  | 7832 | 673 | -1814 | -1814 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 9 | 0 | 9 | 1814 | 1 | AT: 361; AT: 160
20250606 | June | 2330 |  | 7481 | 698 |  | 7471 | 698 | -1391 | -1391 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 10 | 0 | 10 | 1391 | 1 | AT: 361; AT: 160
20250607 | June | 30 | 6904 |  |  | 6903 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 361; AT: 160
20250607 | June | 130 | 6904 |  |  | 6903 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160
20250607 | June | 230 | 6904 |  |  | 6903 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160
20250607 | June | 330 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2446 | 1 | AT: 405; AT: 160
20250607 | June | 430 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2446 | 1 | AT: 405; AT: 160
20250607 | June | 530 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2446 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 630 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2446 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 730 | 8744 |  |  | 8551 |  |  | -2498 | -2498 | -2308 | Critical Branch | Validation phase | 0 | 193 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250607 | June | 830 | 8744 |  |  | 8551 |  |  | -2498 | -2498 | -2308 | Critical Branch | Validation phase | 0 | 193 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250607 | June | 930 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250607 | June | 1030 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250607 | June | 1130 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250607 | June | 1230 | 7530 |  |  | 7529 |  |  | -3991 | -3991 | -3990 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 385; AT: 140
20250607 | June | 1330 | 7530 |  |  | 7529 |  |  | -3991 | -3991 | -3990 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 1430 | 7530 |  |  | 7529 |  |  | -3991 | -3991 | -3990 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 1530 | 8496 |  |  | 8483 |  |  | -3331 | -3331 | -3318 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 1630 | 8496 |  |  | 8483 |  |  | -3331 | -3331 | -3318 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 1730 | 8496 |  |  | 8483 |  |  | -3331 | -3331 | -3318 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 13 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 1830 | 8547 |  |  | 8531 |  |  | -1914 | -1914 | -1904 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250607 | June | 1930 | 8547 |  |  | 8531 |  |  | -1914 | -1914 | -1904 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140
20250607 | June | 2030 | 8547 |  |  | 8531 |  |  | -1914 | -1914 | -1904 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140
20250607 | June | 2130 | 8076 |  |  | 8076 |  |  | -2140 | -2140 | -2140 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 405; AT: 160
20250607 | June | 2230 | 8076 |  |  | 8076 |  |  | -2140 | -2140 | -2140 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250607 | June | 2330 | 7676 |  |  | 7676 |  |  | -1743 | -1743 | -1743 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250608 | June | 30 | 8604 |  |  | 8561 |  |  | -1985 | -1985 | -1946 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250608 | June | 130 | 8604 |  |  | 8561 |  |  | -1985 | -1985 | -1946 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 230 | 8604 |  |  | 8561 |  |  | -1985 | -1985 | -1946 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 43 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 430 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 530 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 630 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 730 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 830 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 930 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 1030 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 1130 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250608 | June | 1230 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 385; AT: 160
20250608 | June | 1330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 291; AT: 160
20250608 | June | 1430 | 7850 |  |  | 7319 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 531 | NA | NA | NA | 0 | 1 | AT: 291; AT: 160
20250608 | June | 1530 |  | 5298 | 451 |  | 5298 | 451 | -2876 | -2876 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2876 | 1 | AT: 291; AT: 160
20250608 | June | 1630 |  | 5298 | 451 |  | 5298 | 451 | -2876 | -2876 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2876 | 1 | AT: 385; AT: 160; FR: 3437; FR: Process fail during TSO validation phase
20250608 | June | 1730 |  | 5298 | 451 |  | 5298 | 451 | -2876 | -2876 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 2876 | 1 | AT: 394; AT: 160
20250608 | June | 1830 |  | 7110 | 668 |  | 6826 | 668 | 877 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 748 | NA | 284 | 0 | 284 | -129 | 1 | AT: 394; AT: 160
20250608 | June | 1930 |  | 6981 | 656 |  | 6981 | 656 | 877 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 877 | NA | 0 | 0 | 0 | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250608 | June | 2030 |  | 6981 | 656 |  | 6981 | 656 | 877 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 877 | NA | 0 | 0 | 0 | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250608 | June | 2130 |  | 8209 | 780 |  | 8155 | 780 | -2724 | -2724 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 54 | 0 | 54 | 2724 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250608 | June | 2230 |  | 8209 | 780 |  | 8155 | 780 | -2724 | -2724 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 54 | 0 | 54 | 2724 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250608 | June | 2330 |  | 8209 | 780 |  | 8155 | 780 | -2724 | -2724 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 54 | 0 | 54 | 2724 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250609 | June | 30 | 8031 |  |  | 8021 |  |  | -2071 | -2071 | -2060 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250609 | June | 130 | 8031 |  |  | 8021 |  |  | -2071 | -2071 | -2060 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250609 | June | 230 | 8031 |  |  | 8021 |  |  | -2071 | -2071 | -2060 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250609 | June | 330 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 1503 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250609 | June | 430 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 1503 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250609 | June | 530 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 1503 | 1 | AT: 339; AT: 140
20250609 | June | 630 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 18 | 0 | 18 | 1503 | 1 | AT: 339; AT: 140
20250609 | June | 730 |  | 6225 | 539 |  | 6225 | 539 | -822 | -822 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 822 | 1 | AT: 409; AT: 140
20250609 | June | 830 |  | 6225 | 539 |  | 6225 | 539 | -822 | -822 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 822 | 1 | AT: 410; AT: 140
20250609 | June | 930 | 7993 |  |  | 7965 |  |  | -5511 | -5511 | -5483 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 28 | NA | NA | NA | 0 | 1 | AT: 404; AT: 140
20250609 | June | 1030 | 7993 |  |  | 7992 |  |  | -5511 | -5511 | -5510 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 333; AT: 138
20250609 | June | 1130 | 7993 |  |  | 7867 |  |  | -5511 | -5511 | -5385 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 126 | NA | NA | NA | 0 | 1 | AT: 333; AT: 138
20250609 | June | 1230 |  | 6131 | 695 |  | 6130 | 695 | -195 | -195 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 195 | 1 | AT: 333; AT: 138
20250609 | June | 1330 |  | 6131 | 695 |  | 6130 | 695 | -195 | -195 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 195 | 1 | AT: 415; AT: 137
20250609 | June | 1430 |  | 6131 | 695 |  | 6130 | 695 | -195 | -195 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 195 | 1 | AT: 415; AT: 137
20250609 | June | 1530 |  | 7518 | 722 |  | 7518 | 722 | -1773 | -1773 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1773 | 1 | AT: 402; AT: 137
20250609 | June | 1630 |  | 7518 | 722 |  | 7518 | 722 | -1773 | -1773 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 1773 | 1 | AT: 305; AT: 140
20250609 | June | 1730 |  | 7518 | 722 |  | 7300 | 722 | -1773 | -1773 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 218 | 0 | 218 | 1773 | 1 | AT: 305; AT: 140
20250609 | June | 1830 |  | 5661 | 399 |  | 5660 | 399 | -2258 | -2258 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2258 | 1 | AT: 305; AT: 140
20250609 | June | 1930 |  | 5661 | 399 |  | 5660 | 399 | -2258 | -2258 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2258 | 1 | AT: 305; AT: 140
20250609 | June | 2030 |  | 5661 | 399 |  | 5660 | 399 | -2258 | -2258 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2258 | 1 | AT: 305; AT: 140
20250609 | June | 2130 |  | 5661 | 453 |  | 5660 | 453 | -2252 | -2252 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2252 | 1 | AT: 292; AT: 160
20250609 | June | 2230 |  | 5661 | 453 |  | 5660 | 453 | -2252 | -2252 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 2252 | 0
20250609 | June | 2330 |  | 5301 | 478 |  | 5300 | 478 | -1848 | -1848 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1848 | 0
20250610 | June | 30 | 7270 |  |  | 7270 |  |  | -1562 | -1562 | -1562 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 130 | 7270 |  |  | 7270 |  |  | -1562 | -1562 | -1562 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 230 | 7270 |  |  | 7270 |  |  | -1562 | -1562 | -1562 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 330 | 6782 |  |  | 6782 |  |  | -1243 | -1243 | -1243 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 430 | 6782 |  |  | 6782 |  |  | -1243 | -1243 | -1243 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 530 | 6782 |  |  | 6782 |  |  | -1243 | -1243 | -1243 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 630 | 6582 |  |  | 6582 |  |  | -1029 | -1029 | -1029 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 730 | 5737 |  |  | 5737 |  |  | -793 | -793 | -793 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 830 | 5737 |  |  | 5737 |  |  | -793 | -793 | -793 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250610 | June | 930 | 5487 |  |  | 5398 |  |  | 469 | 262 | 296 | Minimum Margin | Validation phase | 207 | 89 | NA | NA | NA | 330 | 0
20250610 | June | 1030 | 5458 |  |  | 5398 |  |  | 469 | 233 | 296 | Minimum Margin | Validation phase | 236 | 60 | NA | NA | NA | 359 | 0
20250610 | June | 1130 | 5694 |  |  | 5398 |  |  | 469 | 469 | 296 | Adjustment reached | Validation phase | 0 | 296 | NA | NA | NA | 123 | 0
20250610 | June | 1230 | 6609 |  |  | 6186 |  |  | 818 | 596 | 645 | Minimum Margin | Validation phase | 222 | 423 | NA | NA | NA | 694 | 0
20250610 | June | 1330 | 6609 |  |  | 6186 |  |  | 818 | 596 | 645 | Minimum Margin | Validation phase | 222 | 423 | NA | NA | NA | 694 | 0
20250610 | June | 1430 | 6609 |  |  | 6186 |  |  | 818 | 596 | 645 | Minimum Margin | Validation phase | 222 | 423 | NA | NA | NA | 694 | 0
20250610 | June | 1530 | 7041 |  |  | 7035 |  |  | 2759 | 102 | 2663 | Minimum Margin | Validation phase | 2657 | 6 | NA | NA | NA | 5224 | 1 | CH: 6785; CH: Reduction due to missing redispatch potential
20250610 | June | 1630 | 7109 |  |  | 7098 |  |  | 2759 | 170 | 2600 | Minimum Margin | Validation phase | 2589 | 11 | NA | NA | NA | 5030 | 1 | CH: 6848; CH: Reduction due to missing redispatch potential
20250610 | June | 1730 | 7103 |  |  | 6680 |  |  | 2759 | 164 | 3018 | Minimum Margin | Smoothing ramp | 2595 | 423 | NA | NA | NA | 5872 | 1 | CH: 6843; CH: Reduction due to missing redispatch potential
20250610 | June | 1830 |  | 4776 | 392 |  | 4776 | 392 | -1889 | -1889 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1889 | 0
20250610 | June | 1930 |  | 4776 | 392 |  | 4776 | 392 | -1889 | -1889 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1889 | 0
20250610 | June | 2030 |  | 4776 | 392 |  | 4776 | 392 | -1889 | -1889 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1889 | 0
20250610 | June | 2130 |  | 4776 | 411 |  | 4776 | 411 | -1311 | -1311 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1311 | 0
20250610 | June | 2230 |  | 4776 | 411 |  | 4776 | 411 | -1311 | -1311 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 1311 | 1 | AT: 376; AT: 160
20250610 | June | 2330 |  | 4416 | 436 |  | 4416 | 436 | -911 | -911 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 0 | NA | 0 | 0 | 0 | 911 | 1 | AT: 376; AT: 160
20250611 | June | 30 | 6353 |  |  | 6352 |  |  | -2074 | -2074 | -2073 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 376; AT: 160
20250611 | June | 130 | 6353 |  |  | 6352 |  |  | -2074 | -2074 | -2073 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160
20250611 | June | 230 | 6353 |  |  | 6352 |  |  | -2074 | -2074 | -2073 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160
20250611 | June | 330 | 6591 |  |  | 6590 |  |  | -1134 | -1134 | -1134 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160
20250611 | June | 430 | 6591 |  |  | 6590 |  |  | -1134 | -1134 | -1134 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 391; AT: 160
20250611 | June | 530 | 6591 |  |  | 6590 |  |  | -1134 | -1134 | -1134 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 347; AT: 140
20250611 | June | 630 | 6391 |  |  | 6391 |  |  | -938 | -938 | -937 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 347; AT: 140
20250611 | June | 730 | 5237 |  |  | 5237 |  |  | -1713 | -1713 | -1713 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 381; AT: 140
20250611 | June | 830 | 5237 |  |  | 5237 |  |  | -1713 | -1713 | -1713 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 375; AT: 140
20250611 | June | 930 | 5713 |  |  | 5710 |  |  | 4243 | 89 | 4156 | Minimum Margin | Validation phase | 4154 | 3 | NA | NA | NA | 8223 | 1 | AT: 375; AT: 140
20250611 | June | 1030 | 5624 |  |  | 5624 |  |  | 4243 | 0 | 4243 | Critical Branch | TTC Validation phase - bilateral reduction | 4243 | 0 | NA | NA | NA | 4243 | 1 | AT: 399; AT: 140
20250611 | June | 1130 | 5624 |  |  | 5624 |  |  | 4243 | 0 | 4243 | Critical Branch | TTC Validation phase - bilateral reduction | 4243 | 0 | NA | NA | NA | 4243 | 1 | AT: 399; AT: 140
20250611 | June | 1230 | 5958 |  |  | 5957 |  |  | -3307 | -3307 | -3305 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 399; AT: 140
20250611 | June | 1330 | 5958 |  |  | 5957 |  |  | -3307 | -3307 | -3305 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250611 | June | 1430 | 5958 |  |  | 5957 |  |  | -3307 | -3307 | -3305 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250611 | June | 1530 | 6380 |  |  | 6374 |  |  | -3651 | -3651 | -3643 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250611 | June | 1630 | 6380 |  |  | 6374 |  |  | -3651 | -3651 | -3643 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 132; AT: Reduction because NTC over thermal limit on border
20250611 | June | 1730 | 7280 |  |  | 7275 |  |  | -4570 | -4570 | -4564 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 5 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 132; AT: Reduction because NTC over thermal limit on border
20250611 | June | 1830 |  | 8048 | 834 |  | 7962 | 834 | -2538 | -2538 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 2538 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 132; AT: Reduction because NTC over thermal limit on border
20250611 | June | 1930 |  | 8048 | 834 |  | 7962 | 834 | -2538 | -2538 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 2538 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border
20250611 | June | 2030 |  | 8048 | 834 |  | 7962 | 834 | -2538 | -2538 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 86 | 0 | 86 | 2538 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 135; AT: Reduction because NTC over thermal limit on border
20250611 | June | 2130 |  | 7766 | 783 |  | 7699 | 783 | 471 | 107 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 364 | NA | 67 | 0 | 67 | -107 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250611 | June | 2230 |  | 7665 | 774 |  | 7605 | 774 | 471 | 6 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 465 | NA | 60 | 0 | 60 | -6 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250611 | June | 2330 |  | 7394 | 809 |  | 7326 | 809 | 882 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 768 | NA | 68 | 0 | 68 | -114 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250612 | June | 30 | 8270 |  |  | 6950 |  |  | -4919 | -4919 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1320 | NA | NA | NA | 4919 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250612 | June | 130 | 8270 |  |  | 6950 |  |  | -4919 | -4919 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1320 | NA | NA | NA | 4919 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250612 | June | 230 | 8270 |  |  | 6950 |  |  | -4919 | -4919 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1320 | NA | NA | NA | 4919 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250612 | June | 330 | 7955 |  |  | 6950 |  |  | -4528 | -4528 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1005 | NA | NA | NA | 4528 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250612 | June | 430 | 7955 |  |  | 6950 |  |  | -4528 | -4528 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1005 | NA | NA | NA | 4528 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250612 | June | 530 | 7955 |  |  | 6950 |  |  | -4528 | -4528 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1005 | NA | NA | NA | 4528 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250612 | June | 630 | 7755 |  |  | 6750 |  |  | -4318 | -4318 | 0 | Critical Branch | Scheduled TTC | 0 | 1005 | NA | NA | NA | 4318 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250612 | June | 730 | 7854 |  |  | 7200 |  |  | -4602 | -4602 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 654 | NA | NA | NA | 4602 | 1 | AT: 354; AT: 140
20250612 | June | 830 | 7854 |  |  | 7200 |  |  | -4602 | -4602 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 654 | NA | NA | NA | 4602 | 1 | AT: 354; AT: 140
20250612 | June | 930 | 6094 |  |  | 6093 |  |  | -2913 | -2913 | -2912 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 354; AT: 140
20250612 | June | 1030 | 6094 |  |  | 6093 |  |  | -2913 | -2913 | -2912 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250612 | June | 1130 | 6094 |  |  | 6093 |  |  | -2913 | -2913 | -2912 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250612 | June | 1230 | 7365 |  |  | 7200 |  |  | -1017 | -1017 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 165 | NA | NA | NA | 1017 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250612 | June | 1330 | 7365 |  |  | 7200 |  |  | -1017 | -1017 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 165 | NA | NA | NA | 1017 | 1 | AT: 397; AT: 140
20250612 | June | 1430 | 7365 |  |  | 7200 |  |  | -1017 | -1017 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 165 | NA | NA | NA | 1017 | 1 | AT: 397; AT: 140
20250612 | June | 1530 | 6761 |  |  | 6761 |  |  | -3572 | -3572 | -3572 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 397; AT: 140
20250612 | June | 1630 | 6761 |  |  | 6761 |  |  | -3572 | -3572 | -3572 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 401; AT: 140; FR: 3525; FR: Process fail during TSO validation phase
20250612 | June | 1730 | 6761 |  |  | 6761 |  |  | -3572 | -3572 | -3572 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 395; AT: 140; FR: 3525; FR: Process fail during TSO validation phase
20250612 | June | 1830 |  | 6421 | 630 | 6872 |  |  | 2590 | 168 | 3331 | Minimum Margin | TTC Validation phase - bilateral reduction | 2422 | NA | NA | NA | NA | 6494 | 1 | AT: 395; AT: 140; FR: 3525; FR: Process fail during TSO validation phase
20250612 | June | 1930 |  | 6338 | 621 | 6833 |  |  | 2590 | 85 | 3333 | Minimum Margin | TTC Validation phase - bilateral reduction | 2505 | NA | NA | NA | NA | 6581 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250612 | June | 2030 |  | 6338 | 621 | 6833 |  |  | 2590 | 85 | 3333 | Minimum Margin | TTC Validation phase - bilateral reduction | 2505 | NA | NA | NA | NA | 6581 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250612 | June | 2130 |  | 8174 | 705 | 8250 |  |  | -2191 | -2191 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2191 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250612 | June | 2230 |  | 8174 | 705 | 8250 |  |  | -2191 | -2191 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2191 | 1 | AT: 401; AT: 160
20250612 | June | 2330 |  | 7796 | 730 | 7850 |  |  | -1759 | -1759 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 1759 | 1 | AT: 401; AT: 160
20250613 | June | 30 | 7612 |  |  | 7412 |  |  | -3765 | -3765 | -3565 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 401; AT: 160
20250613 | June | 130 | 7612 |  |  | 7412 |  |  | -3765 | -3765 | -3565 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250613 | June | 230 | 7612 |  |  | 7412 |  |  | -3765 | -3765 | -3565 | Critical Branch | Validation phase | 0 | 200 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250613 | June | 330 | 8492 |  |  | 8329 |  |  | -5501 | -5501 | -5349 | Critical Branch | Validation phase | 0 | 163 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250613 | June | 430 | 8492 |  |  | 8329 |  |  | -5501 | -5501 | -5349 | Critical Branch | Validation phase | 0 | 163 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250613 | June | 530 | 8492 |  |  | 8329 |  |  | -5501 | -5501 | -5349 | Critical Branch | Validation phase | 0 | 163 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250613 | June | 630 | 8292 |  |  | 8129 |  |  | -5293 | -5293 | -5141 | Critical Branch | Validation phase | 0 | 163 | NA | NA | NA | 0 | 1 | AT: 418; AT: 140
20250613 | June | 730 | 8339 |  |  | 8168 |  |  | -2951 | -2951 | -2782 | Critical Branch | Validation phase | 0 | 171 | NA | NA | NA | 0 | 1 | AT: 334; AT: 140
20250613 | June | 830 | 8339 |  |  | 7989 |  |  | -2951 | -2951 | -2606 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 350 | NA | NA | NA | 0 | 1 | AT: 337; AT: 140
20250613 | June | 930 | 6490 |  |  | 6489 |  |  | 4521 | 25 | 4497 | Minimum Margin | TTC Validation phase - bilateral reduction | 4496 | 1 | NA | NA | NA | 8969 | 1 | AT: 337; AT: 140
20250613 | June | 1030 | 6536 |  |  | 6535 |  |  | 4521 | 71 | 4451 | Minimum Margin | TTC Validation phase - bilateral reduction | 4450 | 1 | NA | NA | NA | 8831 | 1 | AT: 342; AT: 140
20250613 | June | 1130 | 6534 |  |  | 6534 |  |  | 4521 | 69 | 4453 | Minimum Margin | TTC Validation phase - bilateral reduction | 4452 | 0 | NA | NA | NA | 8837 | 1 | AT: 342; AT: 140
20250613 | June | 1230 | 6632 |  |  | 6631 |  |  | -822 | -822 | -821 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 342; AT: 140
20250613 | June | 1330 | 6632 |  |  | 6631 |  |  | -822 | -822 | -821 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250613 | June | 1430 | 6632 |  |  | 6631 |  |  | -822 | -822 | -821 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250613 | June | 1530 | 8031 |  |  | 8031 |  |  | -3528 | -3528 | -3528 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140
20250613 | June | 1630 | 8031 |  |  | 8031 |  |  | -3528 | -3528 | -3528 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140
20250613 | June | 1730 | 8031 |  |  | 8031 |  |  | -3528 | -3528 | -3528 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 409; AT: 140
20250613 | June | 1830 | 8470 |  |  |  | 8190 | 644 | -2665 | -2665 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2665 | 1 | AT: 409; AT: 140
20250613 | June | 1930 | 8470 |  |  |  | 8190 | 644 | -2665 | -2665 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2665 | 1 | AT: 421; AT: 140
20250613 | June | 2030 | 8470 |  |  |  | 8190 | 644 | -2665 | -2665 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | NA | NA | NA | 2665 | 1 | AT: 421; AT: 140
20250613 | June | 2130 | 8974 |  |  | 8619 |  |  | -6430 | -6430 | -6075 | Critical Branch | Validation phase | 0 | 355 | NA | NA | NA | 0 | 1 | AT: 411; AT: 160
20250613 | June | 2230 | 8974 |  |  | 8619 |  |  | -6430 | -6430 | -6075 | Critical Branch | Validation phase | 0 | 355 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250613 | June | 2330 | 8374 |  |  | 8019 |  |  | -5826 | -5826 | -5471 | Critical Branch | Validation phase | 0 | 355 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 30 | 9276 |  |  | 8692 |  |  | -2495 | -2495 | -1913 | Critical Branch | Validation phase | 0 | 584 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 130 | 9276 |  |  | 8692 |  |  | -2495 | -2495 | -1913 | Critical Branch | Validation phase | 0 | 584 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 230 | 9276 |  |  | 8692 |  |  | -2495 | -2495 | -1913 | Critical Branch | Validation phase | 0 | 584 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 330 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | 0 | 455 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 430 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | 0 | 455 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 530 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | 0 | 455 | NA | NA | NA | 0 | 1 | AT: 387; AT: 140
20250614 | June | 630 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | 0 | 455 | NA | NA | NA | 0 | 1 | AT: 387; AT: 140
20250614 | June | 730 | 8289 |  |  | 8289 |  |  | -1720 | -1720 | -1720 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140
20250614 | June | 830 | 8289 |  |  | 8289 |  |  | -1720 | -1720 | -1720 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140
20250614 | June | 930 | 8428 |  |  | 8428 |  |  | -1545 | -1545 | -1545 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140
20250614 | June | 1030 | 8428 |  |  | 8428 |  |  | -1545 | -1545 | -1545 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 345; AT: 140
20250614 | June | 1130 | 8428 |  |  | 8428 |  |  | -1545 | -1545 | -1545 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 345; AT: 140
20250614 | June | 1230 | 7441 |  |  | 7441 |  |  | -1559 | -1559 | -1559 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 345; AT: 140
20250614 | June | 1330 | 7441 |  |  | 7441 |  |  | -1559 | -1559 | -1559 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 419; AT: 140
20250614 | June | 1430 | 7441 |  |  | 7441 |  |  | -1559 | -1559 | -1559 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250614 | June | 1530 | 9065 |  |  | 8941 |  |  | -2997 | -2997 | -2874 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 124 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250614 | June | 1630 | 9065 |  |  | 8984 |  |  | -2997 | -2997 | -2916 | Critical Branch | Validation phase | 0 | 81 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250614 | June | 1730 | 9065 |  |  | 8984 |  |  | -2997 | -2997 | -2916 | Critical Branch | Validation phase | 0 | 81 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250614 | June | 1830 |  | 8641 | 668 |  | 8633 | 668 | -238 | -238 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 8 | 0 | 8 | 238 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 139; AT: Reduction because NTC over thermal limit on border
20250614 | June | 1930 |  | 8641 | 668 |  | 8633 | 668 | -238 | -238 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 8 | 0 | 8 | 238 | 1 | AT: 425; AT: 140
20250614 | June | 2030 |  | 8641 | 668 |  | 8633 | 668 | -238 | -238 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 8 | 0 | 8 | 238 | 1 | AT: 425; AT: 140
20250614 | June | 2130 | 9057 |  |  | 9057 |  |  | -2582 | -2582 | -2582 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250614 | June | 2230 | 9057 |  |  | 9057 |  |  | -2582 | -2582 | -2582 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250614 | June | 2330 | 8457 |  |  | 8457 |  |  | -1964 | -1964 | -1964 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 30 | 8910 |  |  | 8858 |  |  | -3702 | -3702 | -3659 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 130 | 8910 |  |  | 8858 |  |  | -3702 | -3702 | -3659 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 230 | 8910 |  |  | 8858 |  |  | -3702 | -3702 | -3659 | Critical Branch | Validation phase | 0 | 52 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 330 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 430 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 530 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 630 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | 0 | 67 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 730 | 8865 |  |  | 8843 |  |  | -3326 | -3326 | -3314 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 830 | 8865 |  |  | 8843 |  |  | -3326 | -3326 | -3314 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 22 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 930 | 8562 |  |  | 8556 |  |  | -1834 | -1834 | -1830 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1030 | 8562 |  |  | 8556 |  |  | -1834 | -1834 | -1830 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 394; AT: 160
20250615 | June | 1130 | 8562 |  |  | 8556 |  |  | -1834 | -1834 | -1830 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 394; AT: 160
20250615 | June | 1230 | 8054 |  |  | 8054 |  |  | -1498 | -1498 | -1497 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 394; AT: 160
20250615 | June | 1330 | 8054 |  |  | 8054 |  |  | -1498 | -1498 | -1497 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1430 | 8054 |  |  | 8054 |  |  | -1498 | -1498 | -1497 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1530 | 9042 |  |  | 9011 |  |  | -1795 | -1795 | -1769 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1630 | 9042 |  |  | 9011 |  |  | -1795 | -1795 | -1769 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1730 | 9042 |  |  | 9011 |  |  | -1795 | -1795 | -1769 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 31 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1830 |  | 8373 | 731 |  | 8348 | 731 | -3476 | -3476 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 25 | 0 | 25 | 3476 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250615 | June | 1930 |  | 8373 | 731 |  | 8348 | 731 | -3476 | -3476 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 25 | 0 | 25 | 3476 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250615 | June | 2030 |  | 8373 | 731 |  | 8348 | 731 | -3476 | -3476 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 25 | 0 | 25 | 3476 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250615 | June | 2130 |  | 8443 | 736 |  | 8127 | 710 | -3957 | -3957 | 0 | Critical Branch | Validation phase | 0 | NA | 316 | 26 | 342 | 3957 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 157; AT: Reduction because NTC over thermal limit on border
20250615 | June | 2230 |  | 8443 | 736 |  | 8127 | 710 | -3957 | -3957 | 0 | Critical Branch | Validation phase | 0 | NA | 316 | 26 | 342 | 3957 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250615 | June | 2330 |  | 8443 | 736 |  | 8127 | 710 | -3957 | -3957 | 0 | Critical Branch | Validation phase | 0 | NA | 316 | 26 | 342 | 3957 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250616 | June | 30 | 9070 |  |  | 8450 |  |  | -2094 | -2094 | -1474 | Critical Branch | Validation phase | 0 | 620 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250616 | June | 130 | 9070 |  |  | 8450 |  |  | -2094 | -2094 | -1474 | Critical Branch | Validation phase | 0 | 620 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250616 | June | 230 | 9070 |  |  | 8450 |  |  | -2094 | -2094 | -1474 | Critical Branch | Validation phase | 0 | 620 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250616 | June | 330 |  | 8643 | 812 |  | 7925 | 750 | -1902 | -1902 | 0 | Critical Branch | Validation phase | 0 | NA | 718 | 62 | 780 | 1902 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250616 | June | 430 |  | 8643 | 812 |  | 7925 | 750 | -1902 | -1902 | 0 | Critical Branch | Validation phase | 0 | NA | 718 | 62 | 780 | 1902 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 154; AT: Reduction because NTC over thermal limit on border
20250616 | June | 530 |  | 8643 | 812 |  | 7925 | 750 | -1902 | -1902 | 0 | Critical Branch | Validation phase | 0 | NA | 718 | 62 | 780 | 1902 | 1 | AT: 412; AT: 140
20250616 | June | 630 |  | 8442 | 812 |  | 7724 | 750 | -1651 | -1651 | 0 | Critical Branch | Validation phase | 0 | NA | 718 | 62 | 780 | 1651 | 1 | AT: 399; AT: 140
20250616 | June | 730 | 8653 |  |  | 8652 |  |  | -2048 | -2048 | -2048 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 323; AT: 140
20250616 | June | 830 | 8653 |  |  | 7750 |  |  | -2048 | -2048 | -1147 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 903 | NA | NA | NA | 0 | 1 | AT: 323; AT: 140
20250616 | June | 930 | 6890 |  |  | 6250 |  |  | 2751 | 160 | 3231 | Minimum Margin | Validation phase | 2591 | 640 | NA | NA | NA | 6302 | 1 | AT: 323; AT: 140
20250616 | June | 1030 | 6890 |  |  | 6250 |  |  | 2751 | 160 | 3231 | Minimum Margin | Validation phase | 2591 | 640 | NA | NA | NA | 6302 | 1 | AT: 348; AT: 140
20250616 | June | 1130 | 6890 |  |  | 6250 |  |  | 2751 | 160 | 3231 | Minimum Margin | Validation phase | 2591 | 640 | NA | NA | NA | 6302 | 1 | AT: 348; AT: 140
20250616 | June | 1230 | 7379 |  |  | 7379 |  |  | 4155 | 160 | 3995 | Minimum Margin | TTC Validation phase - bilateral reduction | 3995 | 0 | NA | NA | NA | 7830 | 1 | AT: 348; AT: 140
20250616 | June | 1330 | 7379 |  |  | 7379 |  |  | 4155 | 160 | 3995 | Minimum Margin | TTC Validation phase - bilateral reduction | 3995 | 0 | NA | NA | NA | 7830 | 1 | AT: 325; AT: 140
20250616 | June | 1430 | 7379 |  |  | 7379 |  |  | 4155 | 160 | 3995 | Minimum Margin | TTC Validation phase - bilateral reduction | 3995 | 0 | NA | NA | NA | 7830 | 1 | AT: 325; AT: 140
20250616 | June | 1530 | 6935 |  |  | 6934 |  |  | 2737 | 153 | 2584 | Minimum Margin | TTC Validation phase - bilateral reduction | 2584 | 1 | NA | NA | NA | 5015 | 1 | AT: 325; AT: 140
20250616 | June | 1630 | 6935 |  |  | 6934 |  |  | 2737 | 153 | 2584 | Minimum Margin | TTC Validation phase - bilateral reduction | 2584 | 1 | NA | NA | NA | 5015 | 1 | AT: 360; AT: 140
20250616 | June | 1730 | 6935 |  |  | 6934 |  |  | 2737 | 153 | 2584 | Minimum Margin | TTC Validation phase - bilateral reduction | 2584 | 1 | NA | NA | NA | 5015 | 1 | AT: 360; AT: 140
20250616 | June | 1830 |  | 7272 | 586 |  | 7271 | 586 | -1747 | -1747 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1747 | 1 | AT: 360; AT: 140
20250616 | June | 1930 |  | 7272 | 586 |  | 7271 | 586 | -1747 | -1747 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1747 | 1 | AT: 340; AT: 140
20250616 | June | 2030 |  | 7272 | 586 |  | 7271 | 586 | -1747 | -1747 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1747 | 1 | AT: 340; AT: 140
20250616 | June | 2130 |  | 6898 | 547 |  | 6897 | 547 | -1115 | -1115 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1115 | 1 | AT: 325; AT: 160
20250616 | June | 2230 |  | 6898 | 547 |  | 6897 | 547 | -1115 | -1115 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 1115 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250616 | June | 2330 |  | 6317 | 572 |  | 6316 | 572 | -494 | -494 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 494 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250617 | June | 30 | 8949 |  |  | 8736 |  |  | -4866 | -4866 | -4649 | Critical Branch | Validation phase | 0 | 213 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250617 | June | 130 | 8949 |  |  | 8736 |  |  | -4866 | -4866 | -4649 | Critical Branch | Validation phase | 0 | 213 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250617 | June | 230 | 8949 |  |  | 8736 |  |  | -4866 | -4866 | -4649 | Critical Branch | Validation phase | 0 | 213 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250617 | June | 330 | 8675 |  |  | 8663 |  |  | -4708 | -4708 | -4693 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250617 | June | 430 | 8675 |  |  | 8663 |  |  | -4708 | -4708 | -4693 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250617 | June | 530 | 8675 |  |  | 8663 |  |  | -4708 | -4708 | -4693 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 339; AT: 140
20250617 | June | 630 | 8475 |  |  | 8463 |  |  | -4500 | -4500 | -4485 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 12 | NA | NA | NA | 0 | 1 | AT: 339; AT: 140
20250617 | June | 730 | 7219 |  |  | 7218 |  |  | -2023 | -2023 | -2023 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 315; AT: 140
20250617 | June | 830 | 7219 |  |  | 7218 |  |  | -2023 | -2023 | -2023 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 315; AT: 140
20250617 | June | 930 | 6730 |  |  | 6730 |  |  | -3515 | -3515 | -3514 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 315; AT: 140
20250617 | June | 1030 | 6730 |  |  | 6730 |  |  | -3515 | -3515 | -3514 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140
20250617 | June | 1130 | 6730 |  |  | 6730 |  |  | -3515 | -3515 | -3514 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1230 | 8900 |  |  | 8230 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 670 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1330 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1430 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1530 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1630 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1730 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1830 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 1930 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 2030 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: 140
20250617 | June | 2130 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250617 | June | 2230 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250617 | June | 2330 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 30 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 330 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 430 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 530 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 630 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 730 | 7995 |  |  | 7995 |  |  | 3153 | 0 | 3153 | Critical Branch | Critical Branch | 3153 | 0 | NA | NA | NA | 3153 | 0
20250618 | June | 830 | 7996 |  |  | 7996 |  |  | 3153 | 1 | 3152 | Minimum Margin | Minimum Margin | 3152 | 0 | NA | NA | NA | 6303 | 0
20250618 | June | 930 | 7458 |  |  | 7458 |  |  | -330 | -330 | -330 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 1030 | 7458 |  |  | 7458 |  |  | -330 | -330 | -330 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 1130 | 7458 |  |  | 7458 |  |  | -330 | -330 | -330 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 1230 | 7425 |  |  | 7425 |  |  | 8255 | 329 | 7926 | Minimum Margin | Minimum Margin | 7926 | 0 | NA | NA | NA | 15523 | 0
20250618 | June | 1330 | 7425 |  |  | 7425 |  |  | 8255 | 329 | 7926 | Minimum Margin | Minimum Margin | 7926 | 0 | NA | NA | NA | 15523 | 0
20250618 | June | 1430 | 7425 |  |  | 7425 |  |  | 8255 | 329 | 7926 | Minimum Margin | Minimum Margin | 7926 | 0 | NA | NA | NA | 15523 | 0
20250618 | June | 1530 | 8782 |  |  | 8782 |  |  | -1640 | -1640 | -1640 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 1630 | 8782 |  |  | 8782 |  |  | -1640 | -1640 | -1640 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250618 | June | 1730 | 8782 |  |  | 8502 |  |  | -1640 | -1640 | -1361 | Critical Branch | Smoothing ramp | 0 | 280 | NA | NA | NA | 0 | 1
20250618 | June | 1830 |  | 6566 | 503 |  | 6566 | 503 | 4051 | 116 | 0 | Minimum Margin | Minimum Margin | 3935 | NA | 0 | 0 | 0 | -116 | 0
20250618 | June | 1930 |  | 6458 | 495 |  | 6458 | 495 | 4051 | 8 | 0 | Minimum Margin | Minimum Margin | 4043 | NA | 0 | 0 | 0 | -8 | 0
20250618 | June | 2030 |  | 6480 | 496 |  | 6480 | 496 | 4051 | 30 | 0 | Minimum Margin | Minimum Margin | 4021 | NA | 0 | 0 | 0 | -30 | 0
20250618 | June | 2130 |  | 7516 | 581 |  | 7516 | 581 | -5544 | -5544 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5544 | 0
20250618 | June | 2230 |  | 7516 | 581 |  | 7516 | 581 | -5544 | -5544 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5544 | 1 | AT: 415; AT: 160
20250618 | June | 2330 |  | 6956 | 606 |  | 6956 | 606 | -4922 | -4922 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4922 | 1 | AT: 415; AT: 160
20250619 | June | 30 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250619 | June | 130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250619 | June | 230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250619 | June | 330 | 8956 |  |  | 8888 |  |  | -6022 | -6022 | -5965 | Critical Branch | Validation phase | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250619 | June | 430 | 8956 |  |  | 8888 |  |  | -6022 | -6022 | -5965 | Critical Branch | Validation phase | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250619 | June | 530 | 8956 |  |  | 8888 |  |  | -6022 | -6022 | -5965 | Critical Branch | Validation phase | 0 | 68 | NA | NA | NA | 0 | 1 | AT: 383; AT: 140
20250619 | June | 630 | 8756 |  |  | 8687 |  |  | -5809 | -5809 | -5751 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 382; AT: 140
20250619 | June | 730 | 8074 |  |  | 8074 |  |  | 3301 | 157 | 3144 | Minimum Margin | TTC Validation phase - bilateral reduction | 3144 | 0 | NA | NA | NA | 6131 | 1 | AT: 357; AT: 140
20250619 | June | 830 | 8053 |  |  | 8053 |  |  | 3301 | 136 | 3165 | Minimum Margin | TTC Validation phase - bilateral reduction | 3165 | 0 | NA | NA | NA | 6194 | 1 | AT: 357; AT: 140
20250619 | June | 930 | 7563 |  |  | 7563 |  |  | -478 | -478 | -478 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 357; AT: 140
20250619 | June | 1030 | 7563 |  |  | 7563 |  |  | -478 | -478 | -478 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 321; AT: 140
20250619 | June | 1130 | 7563 |  |  | 7563 |  |  | -478 | -478 | -478 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 321; AT: 140
20250619 | June | 1230 | 6858 |  |  | 6857 |  |  | -850 | -850 | -849 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 321; AT: 140
20250619 | June | 1330 | 6858 |  |  | 6857 |  |  | -850 | -850 | -849 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 315; AT: 140
20250619 | June | 1430 | 6858 |  |  | 6857 |  |  | -850 | -850 | -849 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 315; AT: 140
20250619 | June | 1530 | 6730 |  |  | 6730 |  |  | -3532 | -3532 | -3532 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 315; AT: 140
20250619 | June | 1630 | 6730 |  |  | 6730 |  |  | -3532 | -3532 | -3532 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 384; AT: 140
20250619 | June | 1730 | 6730 |  |  | 6730 |  |  | -3532 | -3532 | -3532 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250619 | June | 1830 |  | 8546 | 661 |  | 7717 | 661 | 1195 | 155 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1040 | NA | 829 | 0 | 829 | -155 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250619 | June | 1930 |  | 8856 | 685 |  | 8836 | 685 | 1195 | 465 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 730 | NA | 20 | 0 | 20 | -465 | 1 | AT: 410; AT: 140
20250619 | June | 2030 |  | 8856 | 685 |  | 8836 | 685 | 1195 | 465 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 730 | NA | 20 | 0 | 20 | -465 | 1 | AT: 410; AT: 140
20250619 | June | 2130 | 8757 |  |  | 8757 |  |  | -2348 | -2348 | -2348 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 399; AT: 160
20250619 | June | 2230 | 8757 |  |  | 8757 |  |  | -2348 | -2348 | -2348 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0
20250619 | June | 2330 | 8157 |  |  | 8156 |  |  | -1734 | -1734 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0
20250620 | June | 30 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 130 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 230 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 330 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 430 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 530 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 630 | 8250 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 730 | 8900 |  |  | 8400 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 830 | 8900 |  |  | 8400 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 930 | 8900 |  |  | 8400 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 1030 | 8900 |  |  | 8400 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 1130 | 8900 |  |  | 8400 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 1230 | 8900 |  |  | 7879 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1021 | NA | NA | NA | 0 | 1 | SI: 7629; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1330 | 8900 |  |  | 7879 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1021 | NA | NA | NA | 0 | 1 | SI: 7629; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1430 | 8900 |  |  | 7879 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1021 | NA | NA | NA | 0 | 1 | SI: 7629; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1530 | 8900 |  |  | 7704 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1196 | NA | NA | NA | 0 | 1 | SI: 7454; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1630 | 8900 |  |  | 7704 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1196 | NA | NA | NA | 0 | 1 | SI: 7454; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1730 | 8900 |  |  | 7704 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 1196 | NA | NA | NA | 0 | 1 | SI: 7454; SI: Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1830 | 9050 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 1930 | 9050 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 2030 | 9050 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 2130 | 9050 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 0
20250620 | June | 2230 | 9050 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250620 | June | 2330 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 500 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 30 | 9088 |  |  | 9055 |  |  | -2594 | -2594 | -2567 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 33 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 130 | 9088 |  |  | 9055 |  |  | -2594 | -2594 | -2567 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 33 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 230 | 9088 |  |  | 9055 |  |  | -2594 | -2594 | -2567 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 33 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 330 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 430 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 530 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140
20250621 | June | 630 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 394; AT: 140
20250621 | June | 730 | 8437 |  |  | 8436 |  |  | -4975 | -4975 | -4974 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250621 | June | 830 | 8437 |  |  | 8436 |  |  | -4975 | -4975 | -4974 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250621 | June | 930 | 8158 |  |  | 8157 |  |  | -579 | -579 | -578 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250621 | June | 1030 | 8158 |  |  | 8157 |  |  | -579 | -579 | -578 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 326; AT: 140
20250621 | June | 1130 | 8158 |  |  | 8157 |  |  | -579 | -579 | -578 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 326; AT: 140
20250621 | June | 1230 | 7067 |  |  | 7067 |  |  | 187 | 187 | 1 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | -185 | 1 | AT: 326; AT: 140
20250621 | June | 1330 | 7067 |  |  | 7067 |  |  | 187 | 187 | 1 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | -185 | 1 | AT: 380; AT: 140
20250621 | June | 1430 | 7067 |  |  | 7067 |  |  | 187 | 187 | 1 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | -185 | 1 | AT: 380; AT: 140
20250621 | June | 1530 | 8161 |  |  | 8160 |  |  | -1167 | -1167 | -1166 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250621 | June | 1630 | 8161 |  |  | 8160 |  |  | -1167 | -1167 | -1166 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140; FR: 3588; FR: Process fail during TSO validation phase
20250621 | June | 1730 | 8161 |  |  | 8160 |  |  | -1167 | -1167 | -1166 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 421; AT: 140; FR: 3588; FR: Process fail during TSO validation phase
20250621 | June | 1830 |  | 8414 | 651 |  | 8192 | 651 | 2048 | 461 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1587 | NA | 222 | 0 | 222 | -461 | 1 | AT: 421; AT: 140; FR: 3588; FR: Process fail during TSO validation phase
20250621 | June | 1930 |  | 8414 | 651 |  | 8192 | 651 | 2048 | 461 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1587 | NA | 222 | 0 | 222 | -461 | 1 | AT: 360; AT: 140
20250621 | June | 2030 |  | 8414 | 651 |  | 8192 | 651 | 2048 | 461 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1587 | NA | 222 | 0 | 222 | -461 | 1 | AT: 360; AT: 140
20250621 | June | 2130 |  | 7266 | 561 |  | 7266 | 561 | -3761 | -3761 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 3761 | 1 | AT: 347; AT: 160
20250621 | June | 2230 |  | 7266 | 561 |  | 7266 | 561 | -3761 | -3761 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 3761 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250621 | June | 2330 |  | 6706 | 586 |  | 6706 | 586 | -3179 | -3179 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 3179 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 30 | 8873 |  |  | 8500 |  |  | -1927 | -1927 | -1561 | Critical Branch | Validation phase | 0 | 373 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 130 | 8873 |  |  | 8500 |  |  | -1927 | -1927 | -1561 | Critical Branch | Validation phase | 0 | 373 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 230 | 8873 |  |  | 8500 |  |  | -1927 | -1927 | -1561 | Critical Branch | Validation phase | 0 | 373 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 330 | 8687 |  |  | 8373 |  |  | 1145 | 573 | 872 | Minimum Margin | Validation phase | 572 | 314 | NA | NA | NA | 1171 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 430 | 8489 |  |  | 8389 |  |  | 1145 | 375 | 856 | Minimum Margin | Validation phase | 770 | 100 | NA | NA | NA | 1337 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 530 | 8687 |  |  | 8373 |  |  | 1145 | 573 | 872 | Minimum Margin | Validation phase | 572 | 314 | NA | NA | NA | 1171 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 630 | 8529 |  |  | 8393 |  |  | 1145 | 415 | 851 | Minimum Margin | Validation phase | 730 | 136 | NA | NA | NA | 1287 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 730 | 8870 |  |  | 8764 |  |  | -624 | -624 | -524 | Critical Branch | Validation phase | 0 | 106 | NA | NA | NA | 0 | 1 | AT: 372; AT: 160
20250622 | June | 830 | 8870 |  |  | 8004 |  |  | -624 | -624 | 237 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 866 | NA | NA | NA | 1098 | 1 | AT: 372; AT: 160
20250622 | June | 930 | 7089 |  |  | 6504 |  |  | -11 | -11 | 574 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 1159 | 1 | AT: 372; AT: 160
20250622 | June | 1030 | 7089 |  |  | 6504 |  |  | -11 | -11 | 574 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 1159 | 1 | AT: 375; AT: 160
20250622 | June | 1130 | 7089 |  |  | 6504 |  |  | -11 | -11 | 574 | Critical Branch | Validation phase | 0 | 585 | NA | NA | NA | 1159 | 1 | AT: 365; AT: 160
20250622 | June | 1230 | 7151 |  |  | 6402 |  |  | 596 | 463 | 882 | Minimum Margin | Validation phase | 133 | 749 | NA | NA | NA | 1301 | 1 | AT: 379; AT: 160
20250622 | June | 1330 | 6967 |  |  | 6402 |  |  | 596 | 279 | 882 | Minimum Margin | Validation phase | 317 | 565 | NA | NA | NA | 1485 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250622 | June | 1430 | 7226 |  |  | 6402 |  |  | 596 | 538 | 882 | Minimum Margin | Validation phase | 58 | 824 | NA | NA | NA | 1226 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250622 | June | 1530 |  | 7795 | 774 |  | 7617 | 769 | -694 | -694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 178 | 5 | 183 | 694 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 155; AT: Reduction because NTC over thermal limit on border
20250622 | June | 1630 |  | 7795 | 774 |  | 7714 | 769 | -694 | -694 | 0 | Critical Branch | Validation phase | 0 | NA | 81 | 5 | 86 | 694 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20250622 | June | 1730 |  | 7795 | 774 |  | 7714 | 769 | -694 | -694 | 0 | Critical Branch | Validation phase | 0 | NA | 81 | 5 | 86 | 694 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20250622 | June | 1830 |  | 8600 | 821 |  | 8120 | 781 | -6213 | -6213 | 0 | Critical Branch | Validation phase | 0 | NA | 480 | 40 | 520 | 6213 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 153; AT: Reduction because NTC over thermal limit on border
20250622 | June | 1930 |  | 8600 | 821 |  | 8120 | 781 | -6213 | -6213 | 0 | Critical Branch | Validation phase | 0 | NA | 480 | 40 | 520 | 6213 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250622 | June | 2030 |  | 8600 | 821 |  | 8120 | 781 | -6213 | -6213 | 0 | Critical Branch | Validation phase | 0 | NA | 480 | 40 | 520 | 6213 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250622 | June | 2130 |  | 8629 | 827 |  | 8120 | 784 | -6623 | -6623 | 0 | Critical Branch | Validation phase | 0 | NA | 509 | 43 | 552 | 6623 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 152; AT: Reduction because NTC over thermal limit on border
20250622 | June | 2230 |  | 8629 | 827 |  | 8120 | 784 | -6623 | -6623 | 0 | Critical Branch | Validation phase | 0 | NA | 509 | 43 | 552 | 6623 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250622 | June | 2330 |  | 8629 | 827 |  | 8120 | 784 | -6623 | -6623 | 0 | Critical Branch | Validation phase | 0 | NA | 509 | 43 | 552 | 6623 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 30 | 8675 |  |  | 8300 |  |  | -4904 | -4904 | -4539 | Critical Branch | Validation phase | 0 | 375 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 130 | 8675 |  |  | 8300 |  |  | -4904 | -4904 | -4539 | Critical Branch | Validation phase | 0 | 375 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 230 | 8675 |  |  | 8300 |  |  | -4904 | -4904 | -4539 | Critical Branch | Validation phase | 0 | 375 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 330 | 8193 |  |  | 8078 |  |  | -2870 | -2870 | -2761 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 430 | 8193 |  |  | 8078 |  |  | -2870 | -2870 | -2761 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 530 | 8193 |  |  | 8078 |  |  | -2870 | -2870 | -2761 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | AT: 203; AT: 70
20250623 | June | 630 | 7993 |  |  | 7878 |  |  | -2649 | -2649 | -2540 | Critical Branch | Validation phase | 0 | 115 | NA | NA | NA | 0 | 1 | AT: 202; AT: 70
20250623 | June | 730 | 7861 |  |  | 6577 |  |  | -1623 | -1623 | -339 | Critical Branch | Validation phase | 0 | 1284 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250623 | June | 830 | 6861 |  |  | 5577 |  |  | -474 | -474 | 810 | Critical Branch | Validation phase | 0 | 1284 | NA | NA | NA | 2094 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250623 | June | 930 | 7560 |  |  | 6277 |  |  | -961 | -961 | 322 | Critical Branch | Validation phase | 0 | 1283 | NA | NA | NA | 1605 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1030 | 7560 |  |  | 6277 |  |  | -961 | -961 | 322 | Critical Branch | Validation phase | 0 | 1283 | NA | NA | NA | 1605 | 1 | AT: 198; AT: 70
20250623 | June | 1130 | 7560 |  |  | 6277 |  |  | -961 | -961 | 322 | Critical Branch | Validation phase | 0 | 1283 | NA | NA | NA | 1605 | 1 | AT: 195; AT: 70
20250623 | June | 1230 | 6725 |  |  | 5155 |  |  | 227 | 227 | 1570 | Adjustment reached | Validation phase | 0 | 1570 | NA | NA | NA | 2913 | 1 | AT: 198; AT: 70
20250623 | June | 1330 | 6617 |  |  | 5155 |  |  | 227 | 119 | 1570 | Minimum Margin | Validation phase | 108 | 1462 | NA | NA | NA | 3021 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1430 | 6725 |  |  | 5155 |  |  | 227 | 227 | 1570 | Adjustment reached | Validation phase | 0 | 1570 | NA | NA | NA | 2913 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1530 | 7950 |  |  | 6655 |  |  | -1231 | -1231 | 64 | Critical Branch | Smoothing ramp | 0 | 1295 | NA | NA | NA | 1359 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1630 | 7950 |  |  | 6810 |  |  | -1231 | -1231 | -91 | Critical Branch | Validation phase | 0 | 1140 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1730 | 9165 |  |  | 8025 |  |  | -2604 | -2604 | -1464 | Critical Branch | Validation phase | 0 | 1140 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1830 |  | 8632 | 734 |  | 8358 | 714 | -1577 | -1577 | 0 | Critical Branch | Validation phase | 0 | NA | 274 | 20 | 294 | 1577 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 136; AT: Reduction because NTC over thermal limit on border
20250623 | June | 1930 |  | 8632 | 734 |  | 8358 | 714 | -1577 | -1577 | 0 | Critical Branch | Validation phase | 0 | NA | 274 | 20 | 294 | 1577 | 1 | AT: 425; AT: 140
20250623 | June | 2030 |  | 8632 | 734 |  | 8358 | 714 | -1577 | -1577 | 0 | Critical Branch | Validation phase | 0 | NA | 274 | 20 | 294 | 1577 | 1 | AT: 425; AT: 140
20250623 | June | 2130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: 160
20250623 | June | 2230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250623 | June | 2330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250624 | June | 30 | 8261 |  |  | 7840 |  |  | -1695 | -1695 | -1274 | Critical Branch | Validation phase | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250624 | June | 130 | 8261 |  |  | 7840 |  |  | -1695 | -1695 | -1274 | Critical Branch | Validation phase | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250624 | June | 230 | 8261 |  |  | 7840 |  |  | -1695 | -1695 | -1274 | Critical Branch | Validation phase | 0 | 421 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250624 | June | 330 | 8115 |  |  | 7729 |  |  | -1563 | -1563 | -1177 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250624 | June | 430 | 8115 |  |  | 7729 |  |  | -1563 | -1563 | -1177 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250624 | June | 530 | 8115 |  |  | 7729 |  |  | -1563 | -1563 | -1177 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140
20250624 | June | 630 | 7915 |  |  | 7529 |  |  | -1337 | -1337 | -951 | Critical Branch | Validation phase | 0 | 386 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140
20250624 | June | 730 | 7134 |  |  | 6838 |  |  | -1034 | -1034 | -738 | Critical Branch | Validation phase | 0 | 296 | NA | NA | NA | 0 | 1 | AT: 336; AT: 140
20250624 | June | 830 | 7134 |  |  | 6838 |  |  | -1034 | -1034 | -738 | Critical Branch | Validation phase | 0 | 296 | NA | NA | NA | 0 | 1 | AT: 351; AT: 140
20250624 | June | 930 | 5881 |  |  | 5750 |  |  | 421 | 0 | 552 | Critical Branch | Validation phase | 421 | 131 | NA | NA | NA | 1104 | 1 | AT: 341; AT: 140
20250624 | June | 1030 | 6123 |  |  | 5750 |  |  | 421 | 242 | 552 | Minimum Margin | Validation phase | 179 | 373 | NA | NA | NA | 862 | 1 | AT: 320; AT: 140
20250624 | June | 1130 | 5963 |  |  | 5750 |  |  | 421 | 82 | 552 | Minimum Margin | Validation phase | 339 | 213 | NA | NA | NA | 1022 | 1 | AT: 309; AT: 140
20250624 | June | 1230 | 5635 |  |  | 4638 |  |  | 693 | 186 | 1504 | Minimum Margin | Validation phase | 507 | 997 | NA | NA | NA | 2822 | 1 | AT: 323; AT: 140
20250624 | June | 1330 | 5449 |  |  | 4638 |  |  | 693 | 0 | 1504 | Critical Branch | Validation phase | 693 | 811 | NA | NA | NA | 3008 | 1 | AT: 309; AT: 140
20250624 | June | 1430 | 5681 |  |  | 4638 |  |  | 693 | 232 | 1504 | Minimum Margin | Validation phase | 461 | 1043 | NA | NA | NA | 2776 | 1 | AT: 315; AT: 140
20250624 | June | 1530 | 5451 |  |  | 4536 |  |  | 785 | 155 | 1545 | Minimum Margin | Validation phase | 630 | 915 | NA | NA | NA | 2935 | 1 | AT: 315; AT: 140
20250624 | June | 1630 | 6296 |  |  | 5536 |  |  | -341 | -341 | 419 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 1179 | 1 | AT: 404; AT: 137
20250624 | June | 1730 | 6296 |  |  | 5536 |  |  | -341 | -341 | 419 | Critical Branch | Validation phase | 0 | 760 | NA | NA | NA | 1179 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250624 | June | 1830 |  | 8254 | 698 |  | 6782 | 698 | -2495 | -2495 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1472 | 0 | 1472 | 2495 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250624 | June | 1930 |  | 8254 | 698 |  | 8232 | 698 | -2495 | -2495 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 22 | 0 | 22 | 2495 | 1 | AT: 405; AT: 140
20250624 | June | 2030 |  | 8254 | 698 |  | 8233 | 698 | -2495 | -2495 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 21 | 0 | 21 | 2495 | 1 | AT: 405; AT: 140
20250624 | June | 2130 | 8092 |  |  | 7754 |  |  | -1681 | -1681 | -1343 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 1 | AT: 394; AT: 160
20250624 | June | 2230 | 8092 |  |  | 7754 |  |  | -1681 | -1681 | -1343 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 0
20250624 | June | 2330 | 7492 |  |  | 7154 |  |  | -1077 | -1077 | -739 | Critical Branch | Validation phase | 0 | 338 | NA | NA | NA | 0 | 0
20250625 | June | 30 | 7861 |  |  | 7861 |  |  | -4625 | -4625 | -4625 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250625 | June | 130 | 7861 |  |  | 7861 |  |  | -4625 | -4625 | -4625 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250625 | June | 230 | 7861 |  |  | 7861 |  |  | -4625 | -4625 | -4625 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250625 | June | 330 | 8107 |  |  | 7925 |  |  | -440 | -440 | -258 | Critical Branch | Validation phase | 0 | 182 | NA | NA | NA | 0 | 1 | CH: 7675; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 430 | 8107 |  |  | 7925 |  |  | -440 | -440 | -258 | Critical Branch | Validation phase | 0 | 182 | NA | NA | NA | 0 | 1 | CH: 7675; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 530 | 8107 |  |  | 7925 |  |  | -440 | -440 | -258 | Critical Branch | Validation phase | 0 | 182 | NA | NA | NA | 0 | 1 | CH: 7675; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 630 | 7907 |  |  | 7725 |  |  | -207 | -207 | -25 | Critical Branch | Validation phase | 0 | 182 | NA | NA | NA | 0 | 1 | CH: 7475; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 730 | 8077 |  |  | 8077 |  |  | -1706 | -1706 | -1706 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250625 | June | 830 | 8077 |  |  | 8077 |  |  | -1706 | -1706 | -1706 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250625 | June | 930 | 7128 |  |  | 7128 |  |  | 211 | 0 | 211 | Critical Branch | Critical Branch | 211 | 0 | NA | NA | NA | 211 | 0
20250625 | June | 1030 | 7339 |  |  | 7339 |  |  | 211 | 211 | 0 | Adjustment reached | Adjustment reached | 0 | 0 | NA | NA | NA | -211 | 0
20250625 | June | 1130 | 7129 |  |  | 7129 |  |  | 211 | 1 | 210 | Minimum Margin | Minimum Margin | 210 | 0 | NA | NA | NA | 419 | 0
20250625 | June | 1230 | 7739 |  |  | 7341 |  |  | -431 | -431 | -33 | Critical Branch | Validation phase | 0 | 398 | NA | NA | NA | 0 | 1 | CH: 7091; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 1330 | 7739 |  |  | 7341 |  |  | -431 | -431 | -33 | Critical Branch | Validation phase | 0 | 398 | NA | NA | NA | 0 | 1 | CH: 7091; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 1430 | 7739 |  |  | 7341 |  |  | -431 | -431 | -33 | Critical Branch | Validation phase | 0 | 398 | NA | NA | NA | 0 | 1 | CH: 7091; CH: Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 1530 | 7213 |  |  | 7213 |  |  | 111 | 111 | 0 | Adjustment reached | Adjustment reached | 0 | 0 | NA | NA | NA | -111 | 0
20250625 | June | 1630 | 7213 |  |  | 7213 |  |  | 111 | 111 | 0 | Adjustment reached | Adjustment reached | 0 | 0 | NA | NA | NA | -111 | 0
20250625 | June | 1730 | 7702 |  |  | 7702 |  |  | -394 | -394 | -394 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0
20250625 | June | 1830 |  | 7657 | 634 |  | 7657 | 634 | -5121 | -5121 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5121 | 0
20250625 | June | 1930 |  | 7657 | 634 |  | 7657 | 634 | -5121 | -5121 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5121 | 0
20250625 | June | 2030 |  | 7657 | 634 |  | 7657 | 634 | -5121 | -5121 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5121 | 0
20250625 | June | 2130 |  | 7689 | 624 |  | 7689 | 624 | -5123 | -5123 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5123 | 0
20250625 | June | 2230 |  | 7689 | 624 |  | 7689 | 624 | -5123 | -5123 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 5123 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250625 | June | 2330 |  | 7109 | 649 |  | 7109 | 649 | -4495 | -4495 | 0 | Critical Branch | Critical Branch | 0 | NA | 0 | 0 | 0 | 4495 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 30 | 9498 |  |  | 9332 |  |  | -6088 | -6088 | -5940 | Critical Branch | Validation phase | 0 | 166 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 130 | 9498 |  |  | 9332 |  |  | -6088 | -6088 | -5940 | Critical Branch | Validation phase | 0 | 166 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 230 | 9498 |  |  | 9332 |  |  | -6088 | -6088 | -5940 | Critical Branch | Validation phase | 0 | 166 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 330 | 8611 |  |  | 8542 |  |  | -4953 | -4953 | -4886 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 430 | 8611 |  |  | 8542 |  |  | -4953 | -4953 | -4886 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 530 | 8611 |  |  | 8542 |  |  | -4953 | -4953 | -4886 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 630 | 8411 |  |  | 8342 |  |  | -4747 | -4747 | -4679 | Critical Branch | Validation phase | 0 | 69 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 730 | 8248 |  |  | 8191 |  |  | -1641 | -1641 | -1595 | Critical Branch | Validation phase | 0 | 57 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 830 | 8248 |  |  | 8191 |  |  | -1641 | -1641 | -1595 | Critical Branch | Validation phase | 0 | 57 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 930 | 7667 |  |  | 7657 |  |  | -1056 | -1056 | -1047 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1030 | 7667 |  |  | 7657 |  |  | -1056 | -1056 | -1047 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 406; AT: 140
20250626 | June | 1130 | 7667 |  |  | 7657 |  |  | -1056 | -1056 | -1047 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 10 | NA | NA | NA | 0 | 1 | AT: 406; AT: 140
20250626 | June | 1230 | 7196 |  |  | 7195 |  |  | -600 | -600 | -599 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 406; AT: 140
20250626 | June | 1330 | 7196 |  |  | 7195 |  |  | -600 | -600 | -599 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1430 | 7196 |  |  | 7195 |  |  | -600 | -600 | -599 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1530 | 7623 |  |  | 7616 |  |  | -1232 | -1232 | -1225 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1630 | 7623 |  |  | 7616 |  |  | -1232 | -1232 | -1225 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1730 | 9023 |  |  | 9017 |  |  | -2910 | -2910 | -2904 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 6 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1830 | 9645 |  |  | 9086 |  |  | -1989 | -1989 | -1430 | Critical Branch | Validation phase | 0 | 559 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 1930 | 9645 |  |  | 9086 |  |  | -1989 | -1989 | -1430 | Critical Branch | Validation phase | 0 | 559 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 2030 | 9645 |  |  | 9086 |  |  | -1989 | -1989 | -1430 | Critical Branch | Validation phase | 0 | 559 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250626 | June | 2130 | 9673 |  |  | 8975 |  |  | -2568 | -2568 | -1870 | Critical Branch | Validation phase | 0 | 698 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 2230 | 9673 |  |  | 8975 |  |  | -2568 | -2568 | -1870 | Critical Branch | Validation phase | 0 | 698 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250626 | June | 2330 | 9073 |  |  | 8375 |  |  | -1946 | -1946 | -1248 | Critical Branch | Validation phase | 0 | 698 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250627 | June | 30 | 9115 |  |  | 8753 |  |  | -5089 | -5089 | -4734 | Critical Branch | Validation phase | 0 | 362 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250627 | June | 130 | 9115 |  |  | 8753 |  |  | -5089 | -5089 | -4734 | Critical Branch | Validation phase | 0 | 362 | NA | NA | NA | 0 | 1 | AT: 406; AT: 160
20250627 | June | 230 | 9115 |  |  | 8753 |  |  | -5089 | -5089 | -4734 | Critical Branch | Validation phase | 0 | 362 | NA | NA | NA | 0 | 1 | AT: 406; AT: 160
20250627 | June | 330 | 8283 |  |  | 8227 |  |  | -4041 | -4041 | -3985 | Critical Branch | Validation phase | 0 | 56 | NA | NA | NA | 0 | 1 | AT: 406; AT: 160
20250627 | June | 430 | 8283 |  |  | 8227 |  |  | -4041 | -4041 | -3985 | Critical Branch | Validation phase | 0 | 56 | NA | NA | NA | 0 | 1 | AT: 406; AT: 160
20250627 | June | 530 | 8283 |  |  | 8227 |  |  | -4041 | -4041 | -3985 | Critical Branch | Validation phase | 0 | 56 | NA | NA | NA | 0 | 1 | AT: 402; AT: 140
20250627 | June | 630 | 8083 |  |  | 8027 |  |  | -3826 | -3826 | -3770 | Critical Branch | Validation phase | 0 | 56 | NA | NA | NA | 0 | 1 | AT: 402; AT: 140
20250627 | June | 730 | 8455 |  |  | 8417 |  |  | -4731 | -4731 | -4693 | Critical Branch | Validation phase | 0 | 38 | NA | NA | NA | 0 | 1 | AT: 338; AT: 140
20250627 | June | 830 | 8455 |  |  | 8417 |  |  | -4731 | -4731 | -4693 | Critical Branch | Validation phase | 0 | 38 | NA | NA | NA | 0 | 1 | AT: 338; AT: 140
20250627 | June | 930 | 7200 |  |  | 7199 |  |  | -3620 | -3620 | -3618 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 338; AT: 140
20250627 | June | 1030 | 7200 |  |  | 7199 |  |  | -3620 | -3620 | -3618 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 414; AT: 140
20250627 | June | 1130 | 7200 |  |  | 7199 |  |  | -3620 | -3620 | -3618 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140
20250627 | June | 1230 | 8705 |  |  | 8620 |  |  | -750 | -750 | -665 | Critical Branch | Validation phase | 0 | 85 | NA | NA | NA | 0 | 1 | AT: 415; AT: 140
20250627 | June | 1330 | 8705 |  |  | 8620 |  |  | -750 | -750 | -665 | Critical Branch | Validation phase | 0 | 85 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250627 | June | 1430 | 8705 |  |  | 8620 |  |  | -750 | -750 | -665 | Critical Branch | Validation phase | 0 | 85 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250627 | June | 1530 | 8851 |  |  | 8678 |  |  | -4595 | -4595 | -4422 | Critical Branch | Validation phase | 0 | 173 | NA | NA | NA | 0 | 1 | AT: 422; AT: 140
20250627 | June | 1630 | 8851 |  |  | 8678 |  |  | -4595 | -4595 | -4422 | Critical Branch | Validation phase | 0 | 173 | NA | NA | NA | 0 | 1 | AT: 393; AT: 140
20250627 | June | 1730 | 8851 |  |  | 8678 |  |  | -4595 | -4595 | -4422 | Critical Branch | Validation phase | 0 | 173 | NA | NA | NA | 0 | 1 | AT: 393; AT: 140
20250627 | June | 1830 |  | 7895 | 634 |  | 7894 | 634 | -4990 | -4990 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 4990 | 1 | AT: 393; AT: 140
20250627 | June | 1930 |  | 7895 | 634 |  | 7894 | 634 | -4990 | -4990 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 4990 | 1 | AT: 408; AT: 139
20250627 | June | 2030 |  | 7895 | 634 |  | 7894 | 634 | -4990 | -4990 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 4990 | 1 | AT: 408; AT: 139
20250627 | June | 2130 |  | 8166 | 663 |  | 8166 | 663 | -5565 | -5565 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 5565 | 1 | AT: 396; AT: 159
20250627 | June | 2230 |  | 8166 | 663 |  | 8166 | 663 | -5565 | -5565 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 5565 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250627 | June | 2330 |  | 7586 | 688 |  | 7586 | 688 | -4933 | -4933 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 4933 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 30 | 9269 |  |  | 8986 |  |  | -5728 | -5728 | -5456 | Critical Branch | Validation phase | 0 | 283 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 130 | 9269 |  |  | 8986 |  |  | -5728 | -5728 | -5456 | Critical Branch | Validation phase | 0 | 283 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 230 | 9269 |  |  | 8986 |  |  | -5728 | -5728 | -5456 | Critical Branch | Validation phase | 0 | 283 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 330 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 430 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 530 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250628 | June | 630 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | 0 | 262 | NA | NA | NA | 0 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250628 | June | 730 | 9102 |  |  | 9099 |  |  | -5936 | -5936 | -5933 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 3 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250628 | June | 830 | 9102 |  |  | 9099 |  |  | -5936 | -5936 | -5933 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 3 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250628 | June | 930 | 8164 |  |  | 8163 |  |  | -212 | -212 | -211 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 380; AT: 140
20250628 | June | 1030 | 8164 |  |  | 8163 |  |  | -212 | -212 | -211 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 350; AT: 140
20250628 | June | 1130 | 8164 |  |  | 8163 |  |  | -212 | -212 | -211 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | AT: 350; AT: 140
20250628 | June | 1230 | 7542 |  |  | 7542 |  |  | -433 | -433 | -432 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 350; AT: 140
20250628 | June | 1330 | 7542 |  |  | 7542 |  |  | -433 | -433 | -432 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140
20250628 | June | 1430 | 7542 |  |  | 7542 |  |  | -433 | -433 | -432 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 391; AT: 140
20250628 | June | 1530 |  | 7845 | 629 |  | 7784 | 624 | -693 | -693 | 0 | Critical Branch | Validation phase | 0 | NA | 61 | 5 | 66 | 693 | 1 | AT: 391; AT: 140
20250628 | June | 1630 |  | 7845 | 629 |  | 7784 | 624 | -693 | -693 | 0 | Critical Branch | Validation phase | 0 | NA | 61 | 5 | 66 | 693 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250628 | June | 1730 |  | 7845 | 629 |  | 7784 | 624 | -693 | -693 | 0 | Critical Branch | Validation phase | 0 | NA | 61 | 5 | 66 | 693 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250628 | June | 1830 |  | 8915 | 721 |  | 8892 | 721 | -2490 | -2490 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 23 | 0 | 23 | 2490 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 137; AT: Reduction because NTC over thermal limit on border
20250628 | June | 1930 |  | 8915 | 721 |  | 8892 | 721 | -2490 | -2490 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 23 | 0 | 23 | 2490 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250628 | June | 2030 |  | 8915 | 721 |  | 8892 | 721 | -2490 | -2490 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 23 | 0 | 23 | 2490 | 1 | AT: 425; AT: Reduction because NTC over thermal limit on border; AT: 140; AT: Reduction because NTC over thermal limit on border
20250628 | June | 2130 | 9229 |  |  | 8234 |  |  | -2487 | -2487 | -1492 | Critical Branch | Validation phase | 0 | 995 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 2230 | 9229 |  |  | 8234 |  |  | -2487 | -2487 | -1492 | Critical Branch | Validation phase | 0 | 995 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250628 | June | 2330 | 8629 |  |  | 7634 |  |  | -1871 | -1871 | -876 | Critical Branch | Validation phase | 0 | 995 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 30 | 9304 |  |  | 8942 |  |  | -3681 | -3681 | -3331 | Critical Branch | Validation phase | 0 | 362 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 130 | 9304 |  |  | 8942 |  |  | -3681 | -3681 | -3331 | Critical Branch | Validation phase | 0 | 362 | NA | NA | NA | 0 | 1 | AT: 412; AT: 160
20250629 | June | 230 | 9304 |  |  | 8942 |  |  | -3681 | -3681 | -3331 | Critical Branch | Validation phase | 0 | 362 | NA | NA | NA | 0 | 1 | AT: 412; AT: 160
20250629 | June | 330 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 412; AT: 160
20250629 | June | 430 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 412; AT: 160
20250629 | June | 530 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 630 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 730 | 8870 |  |  | 8688 |  |  | -1915 | -1915 | -1735 | Critical Branch | Validation phase | 0 | 182 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160
20250629 | June | 830 | 8870 |  |  | 8688 |  |  | -1915 | -1915 | -1735 | Critical Branch | Validation phase | 0 | 182 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160
20250629 | June | 930 | 7665 |  |  | 7630 |  |  | -968 | -968 | -933 | Critical Branch | Validation phase | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 374; AT: 160
20250629 | June | 1030 | 7665 |  |  | 7630 |  |  | -968 | -968 | -933 | Critical Branch | Validation phase | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 352; AT: 160
20250629 | June | 1130 | 7665 |  |  | 7630 |  |  | -968 | -968 | -933 | Critical Branch | Validation phase | 0 | 35 | NA | NA | NA | 0 | 1 | AT: 352; AT: 160
20250629 | June | 1230 | 7248 |  |  | 7225 |  |  | -766 | -766 | -743 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 352; AT: 160
20250629 | June | 1330 | 7248 |  |  | 7225 |  |  | -766 | -766 | -743 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250629 | June | 1430 | 7248 |  |  | 7225 |  |  | -766 | -766 | -743 | Critical Branch | Validation phase | 0 | 23 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250629 | June | 1530 |  | 8130 | 720 |  | 8119 | 720 | -1871 | -1871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 11 | 0 | 11 | 1871 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 158; AT: Reduction because NTC over thermal limit on border
20250629 | June | 1630 |  | 8130 | 720 |  | 8119 | 720 | -1871 | -1871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 11 | 0 | 11 | 1871 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 1730 |  | 8130 | 720 |  | 8119 | 720 | -1871 | -1871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 11 | 0 | 11 | 1871 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 1830 | 9656 |  |  | 8385 |  |  | -5475 | -5475 | -4204 | Critical Branch | Validation phase | 0 | 1271 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 1930 | 9656 |  |  | 8385 |  |  | -5475 | -5475 | -4204 | Critical Branch | Validation phase | 0 | 1271 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 2030 | 9656 |  |  | 8385 |  |  | -5475 | -5475 | -4204 | Critical Branch | Validation phase | 0 | 1271 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 2130 | 9290 |  |  | 8345 |  |  | -5636 | -5636 | -4691 | Critical Branch | Validation phase | 0 | 945 | NA | NA | NA | 0 | 1 | AT: 415; AT: Reduction because NTC over thermal limit on border; AT: 160; AT: Reduction because NTC over thermal limit on border
20250629 | June | 2230 | 9290 |  |  | 8345 |  |  | -5636 | -5636 | -4691 | Critical Branch | Validation phase | 0 | 945 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250629 | June | 2330 | 9290 |  |  | 8345 |  |  | -5636 | -5636 | -4691 | Critical Branch | Validation phase | 0 | 945 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 30 | 8402 |  |  | 7974 |  |  | -1203 | -1203 | -789 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 130 | 8402 |  |  | 7974 |  |  | -1203 | -1203 | -789 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 230 | 8402 |  |  | 7974 |  |  | -1203 | -1203 | -789 | Critical Branch | Validation phase | 0 | 428 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 330 | 8628 |  |  | 8341 |  |  | -4469 | -4469 | -4256 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Planned outage of Piossasco-Grande-Ile 1 HVDC
20250630 | June | 430 | 8628 |  |  | 8341 |  |  | -4469 | -4469 | -4256 | Critical Branch | Validation phase | 0 | 287 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border; FR: 3000; FR: Planned outage of Piossasco-Grande-Ile 1 HVDC
20250630 | June | 530 | 8628 |  |  | 7678 |  |  | -4469 | -4469 | -3330 | Critical Branch | Validation phase | 0 | 950 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 630 | 8428 |  |  | 7476 |  |  | -4298 | -4298 | -3166 | Critical Branch | Validation phase | 0 | 952 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 730 | 7383 |  |  | 7245 |  |  | -4170 | -4170 | -3967 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 138 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 830 | 7383 |  |  | 7245 |  |  | -4170 | -4170 | -3967 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 138 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 930 | 6899 |  |  | 6785 |  |  | -1687 | -1687 | -1569 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 114 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1030 | 6899 |  |  | 6785 |  |  | -1687 | -1687 | -1569 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 114 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1130 | 6899 |  |  | 6785 |  |  | -1687 | -1687 | -1569 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 114 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1230 | 6730 |  |  | 6377 |  |  | -1219 | -1219 | -865 | TTC Selection - LTTC | Validation phase | 0 | 353 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1330 | 6730 |  |  | 6377 |  |  | -1219 | -1219 | -865 | TTC Selection - LTTC | Validation phase | 0 | 353 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1430 | 6730 |  |  | 6377 |  |  | -1219 | -1219 | -865 | TTC Selection - LTTC | Validation phase | 0 | 353 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1530 | 7306 |  |  | 6386 |  |  | -313 | -313 | 609 | Critical Branch | Validation phase | 0 | 920 | NA | NA | NA | 1531 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1630 | 7306 |  |  | 6386 |  |  | -313 | -313 | 609 | Critical Branch | Validation phase | 0 | 920 | NA | NA | NA | 1531 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1730 | 7306 |  |  | 6386 |  |  | -313 | -313 | 609 | Critical Branch | Validation phase | 0 | 920 | NA | NA | NA | 1531 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1830 | 8202 |  |  | 7459 |  |  | -966 | -966 | -229 | Critical Branch | Validation phase | 0 | 743 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 1930 | 8202 |  |  | 7459 |  |  | -966 | -966 | -229 | Critical Branch | Validation phase | 0 | 743 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 2030 | 8202 |  |  | 7459 |  |  | -966 | -966 | -229 | Critical Branch | Validation phase | 0 | 743 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 2130 | 8527 |  |  | 7778 |  |  | -1394 | -1394 | -654 | Critical Branch | Validation phase | 0 | 749 | NA | NA | NA | 0 | 1 | AT: 210; AT: Reduction because NTC over thermal limit on border; AT: 70; AT: Reduction because NTC over thermal limit on border
20250630 | June | 2230 | 8527 |  |  | 7778 |  |  | -1394 | -1394 | -654 | Critical Branch | Validation phase | 0 | 749 | NA | NA | NA | 0 | 0
20250630 | June | 2330 | 7927 |  |  | 7191 |  |  | -780 | -780 | -52 | Critical Branch | Validation phase | 0 | 736 | NA | NA | NA | 0 | 0

## DA 70% Reduction
DA 70% reduction results
|  |  | TTC Adjustment |  |  | ANTC |  | LimitedBy
BD | Month | TS | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | Adjustment | 70% reduction | % reduction | Category
20250401 | 730 | April |  | 8191 | 1067 | 3379 | 185 | Minimum Margin | 3194 | 94.53% | above 1000 MW
20250401 | 830 | April |  | 8191 | 1067 | 3379 | 185 | Minimum Margin | 3194 | 94.53% | above 1000 MW
20250401 | 930 | April | 7225 |  |  | 3929 | 235 | Minimum Margin | 3694 | 94.02% | above 1000 MW
20250401 | 1030 | April | 7225 |  |  | 3929 | 235 | Minimum Margin | 3694 | 94.02% | above 1000 MW
20250401 | 1130 | April | 7225 |  |  | 3929 | 235 | Minimum Margin | 3694 | 94.02% | above 1000 MW
20250402 | 930 | April | 7250 |  |  | 972 | 260 | Minimum Margin | 712 | 73.25% | [500-1000] MW
20250402 | 1030 | April | 7244 |  |  | 972 | 254 | Minimum Margin | 718 | 73.87% | [500-1000] MW
20250402 | 1130 | April | 7243 |  |  | 972 | 253 | Minimum Margin | 719 | 73.97% | [500-1000] MW
20250402 | 1230 | April | 8495 |  |  | 1412 | 273 | Minimum Margin | 1139 | 80.67% | above 1000 MW
20250402 | 1330 | April | 8495 |  |  | 1412 | 273 | Minimum Margin | 1139 | 80.67% | above 1000 MW
20250402 | 1430 | April | 8495 |  |  | 1412 | 273 | Minimum Margin | 1139 | 80.67% | above 1000 MW
20250404 | 30 | April | 7025 |  |  | 1910 | 196 | Minimum Margin | 1714 | 89.74% | above 1000 MW
20250404 | 130 | April | 7025 |  |  | 1910 | 196 | Minimum Margin | 1714 | 89.74% | above 1000 MW
20250404 | 230 | April | 7025 |  |  | 1910 | 196 | Minimum Margin | 1714 | 89.74% | above 1000 MW
20250404 | 330 | April | 6699 |  |  | 3428 | 219 | Minimum Margin | 3209 | 93.61% | above 1000 MW
20250404 | 430 | April | 6699 |  |  | 3428 | 219 | Minimum Margin | 3209 | 93.61% | above 1000 MW
20250404 | 530 | April | 6699 |  |  | 3428 | 219 | Minimum Margin | 3209 | 93.61% | above 1000 MW
20250404 | 630 | April | 6493 |  |  | 3394 | 213 | Minimum Margin | 3181 | 93.72% | above 1000 MW
20250404 | 730 | April |  | 6584 | 520 | 3485 | 202 | Minimum Margin | 3283 | 94.2% | above 1000 MW
20250404 | 830 | April |  | 6621 | 523 | 3485 | 239 | Minimum Margin | 3246 | 93.14% | above 1000 MW
20250404 | 1530 | April | 7248 |  |  | 3921 | 258 | Minimum Margin | 3663 | 93.42% | above 1000 MW
20250404 | 1630 | April | 7248 |  |  | 3921 | 258 | Minimum Margin | 3663 | 93.42% | above 1000 MW
20250404 | 1730 | April | 7633 |  |  | 2897 | 243 | Minimum Margin | 2654 | 91.61% | above 1000 MW
20250404 | 1830 | April | 7771 |  |  | 5953 | 181 | Minimum Margin | 5772 | 96.96% | above 1000 MW
20250404 | 1930 | April | 7771 |  |  | 5953 | 181 | Minimum Margin | 5772 | 96.96% | above 1000 MW
20250404 | 2030 | April | 7771 |  |  | 5953 | 181 | Minimum Margin | 5772 | 96.96% | above 1000 MW
20250404 | 2130 | April | 7776 |  |  | 4813 | 186 | Minimum Margin | 4627 | 96.14% | above 1000 MW
20250404 | 2230 | April | 7776 |  |  | 4813 | 186 | Minimum Margin | 4627 | 96.14% | above 1000 MW
20250404 | 2330 | April | 6956 |  |  | 5025 | 176 | Minimum Margin | 4849 | 96.5% | above 1000 MW
20250405 | 30 | April | 6880 |  |  | 437 | 0 | TTC Selection - LTTC | 437 | 100% | below 500 MW
20250405 | 130 | April | 7081 |  |  | 437 | 201 | Minimum Margin | 236 | 54% | below 500 MW
20250405 | 230 | April | 7118 |  |  | 437 | 238 | Minimum Margin | 199 | 45.54% | below 500 MW
20250405 | 330 | April | 7108 |  |  | 390 | 228 | Minimum Margin | 162 | 41.54% | below 500 MW
20250405 | 430 | April | 7103 |  |  | 390 | 223 | Minimum Margin | 167 | 42.82% | below 500 MW
20250405 | 530 | April | 7089 |  |  | 390 | 209 | Minimum Margin | 181 | 46.41% | below 500 MW
20250405 | 630 | April | 7113 |  |  | 390 | 233 | Minimum Margin | 157 | 40.26% | below 500 MW
20250405 | 730 | April | 7801 |  |  | 677 | 211 | Minimum Margin | 466 | 68.83% | [500-1000] MW
20250405 | 830 | April | 7796 |  |  | 677 | 206 | Minimum Margin | 471 | 69.57% | [500-1000] MW
20250405 | 1830 | April | 7801 |  |  | 869 | 211 | Minimum Margin | 658 | 75.72% | [500-1000] MW
20250405 | 1930 | April | 7801 |  |  | 869 | 211 | Minimum Margin | 658 | 75.72% | [500-1000] MW
20250405 | 2030 | April | 7801 |  |  | 869 | 211 | Minimum Margin | 658 | 75.72% | [500-1000] MW
20250405 | 2130 | April | 7767 |  |  | 666 | 177 | Minimum Margin | 489 | 73.42% | [500-1000] MW
20250405 | 2230 | April | 7767 |  |  | 666 | 177 | Minimum Margin | 489 | 73.42% | [500-1000] MW
20250405 | 2330 | April | 6947 |  |  | 1080 | 167 | Minimum Margin | 913 | 84.54% | above 1000 MW
20250407 | 330 | April |  | 7501 | 734 | 335 | 179 | Minimum Margin | 156 | 46.57% | below 500 MW
20250407 | 430 | April |  | 7501 | 734 | 335 | 179 | Minimum Margin | 156 | 46.57% | below 500 MW
20250407 | 530 | April |  | 7501 | 734 | 335 | 179 | Minimum Margin | 156 | 46.57% | below 500 MW
20250407 | 630 | April |  | 7335 | 737 | 343 | 213 | Minimum Margin | 130 | 37.9% | below 500 MW
20250408 | 330 | April |  | 7163 | 665 | 2086 | 222 | Minimum Margin | 1864 | 89.36% | above 1000 MW
20250408 | 430 | April |  | 7163 | 665 | 2086 | 222 | Minimum Margin | 1864 | 89.36% | above 1000 MW
20250408 | 530 | April |  | 7163 | 665 | 2086 | 222 | Minimum Margin | 1864 | 89.36% | above 1000 MW
20250408 | 630 | April |  | 6767 | 647 | 2112 | 25 | Minimum Margin | 2087 | 98.82% | above 1000 MW
20250408 | 1230 | April | 7296 |  |  | 8747 | 256 | Minimum Margin | 8491 | 97.07% | above 1000 MW
20250408 | 1330 | April | 7296 |  |  | 8747 | 256 | Minimum Margin | 8491 | 97.07% | above 1000 MW
20250408 | 1430 | April | 7295 |  |  | 8747 | 255 | Minimum Margin | 8492 | 97.08% | above 1000 MW
20250408 | 1830 | April |  | 7506 | 793 | 6744 | 174 | Minimum Margin | 6570 | 97.42% | above 1000 MW
20250408 | 1930 | April |  | 7441 | 787 | 6744 | 109 | Minimum Margin | 6635 | 98.38% | above 1000 MW
20250408 | 2030 | April |  | 7523 | 795 | 6744 | 191 | Minimum Margin | 6553 | 97.17% | above 1000 MW
20250409 | 730 | April |  | 6146 | 579 | 7943 | 78 | Minimum Margin | 7865 | 99.02% | above 1000 MW
20250409 | 830 | April |  | 6146 | 579 | 7943 | 78 | Minimum Margin | 7865 | 99.02% | above 1000 MW
20250410 | 730 | April |  | 6434 | 395 | 6894 | 2 | Minimum Margin | 6892 | 99.97% | above 1000 MW
20250410 | 830 | April |  | 6649 | 413 | 6894 | 218 | Minimum Margin | 6676 | 96.84% | above 1000 MW
20250410 | 1230 | April | 8254 |  |  | 5989 | 214 | Minimum Margin | 5775 | 96.43% | above 1000 MW
20250410 | 1330 | April | 8254 |  |  | 5989 | 214 | Minimum Margin | 5775 | 96.43% | above 1000 MW
20250410 | 1430 | April | 8254 |  |  | 5989 | 214 | Minimum Margin | 5775 | 96.43% | above 1000 MW
20250410 | 2130 | April | 7486 |  |  | 5684 | 246 | Minimum Margin | 5438 | 95.67% | above 1000 MW
20250410 | 2230 | April | 7489 |  |  | 5684 | 249 | Minimum Margin | 5435 | 95.62% | above 1000 MW
20250410 | 2330 | April | 6664 |  |  | 5905 | 234 | Minimum Margin | 5671 | 96.04% | above 1000 MW
20250411 | 30 | April | 7080 |  |  | 2688 | 200 | Minimum Margin | 2488 | 92.56% | above 1000 MW
20250411 | 130 | April | 7069 |  |  | 2688 | 189 | Minimum Margin | 2499 | 92.97% | above 1000 MW
20250411 | 230 | April | 7047 |  |  | 2688 | 167 | Minimum Margin | 2521 | 93.79% | above 1000 MW
20250411 | 1230 | April | 8123 |  |  | 4398 | 204 | Minimum Margin | 4194 | 95.36% | above 1000 MW
20250411 | 1330 | April | 8123 |  |  | 4398 | 204 | Minimum Margin | 4194 | 95.36% | above 1000 MW
20250411 | 1430 | April | 8123 |  |  | 4398 | 204 | Minimum Margin | 4194 | 95.36% | above 1000 MW
20250411 | 1830 | April |  | 7573 | 489 | 3464 | 107 | Minimum Margin | 3357 | 96.91% | above 1000 MW
20250411 | 1930 | April |  | 7610 | 492 | 3464 | 144 | Minimum Margin | 3320 | 95.84% | above 1000 MW
20250411 | 2030 | April |  | 7672 | 496 | 3464 | 207 | Minimum Margin | 3257 | 94.02% | above 1000 MW
20250411 | 2130 | April | 8252 |  |  | 3499 | 162 | Minimum Margin | 3337 | 95.37% | above 1000 MW
20250411 | 2230 | April | 8287 |  |  | 3499 | 197 | Minimum Margin | 3302 | 94.37% | above 1000 MW
20250411 | 2330 | April | 7454 |  |  | 3756 | 174 | Minimum Margin | 3582 | 95.37% | above 1000 MW
20250412 | 330 | April | 7610 |  |  | 3216 | 230 | Minimum Margin | 2986 | 92.85% | above 1000 MW
20250412 | 430 | April | 7553 |  |  | 3216 | 173 | Minimum Margin | 3043 | 94.62% | above 1000 MW
20250412 | 530 | April | 7599 |  |  | 3216 | 219 | Minimum Margin | 2997 | 93.19% | above 1000 MW
20250412 | 630 | April | 7598 |  |  | 3216 | 218 | Minimum Margin | 2998 | 93.22% | above 1000 MW
20250412 | 1830 | April | 8328 |  |  | 3341 | 131 | Minimum Margin | 3210 | 96.08% | above 1000 MW
20250412 | 1930 | April | 8414 |  |  | 3341 | 217 | Minimum Margin | 3124 | 93.5% | above 1000 MW
20250412 | 2030 | April | 8385 |  |  | 3341 | 188 | Minimum Margin | 3153 | 94.37% | above 1000 MW
20250413 | 1830 | April |  | 7840 | 618 | 2818 | 169 | Minimum Margin | 2649 | 94% | above 1000 MW
20250413 | 1930 | April |  | 7888 | 622 | 2818 | 217 | Minimum Margin | 2601 | 92.3% | above 1000 MW
20250413 | 2030 | April |  | 7777 | 613 | 2818 | 106 | Minimum Margin | 2712 | 96.24% | above 1000 MW
20250413 | 2130 | April | 8403 |  |  | 4720 | 56 | Minimum Margin | 4664 | 98.81% | above 1000 MW
20250413 | 2230 | April | 8525 |  |  | 4720 | 178 | Minimum Margin | 4542 | 96.23% | above 1000 MW
20250413 | 2330 | April | 8499 |  |  | 4720 | 152 | Minimum Margin | 4568 | 96.78% | above 1000 MW
20250416 | 30 | April | 7045 |  |  | 2149 | 222 | Minimum Margin | 1927 | 89.67% | above 1000 MW
20250416 | 130 | April | 7045 |  |  | 2149 | 222 | Minimum Margin | 1927 | 89.67% | above 1000 MW
20250416 | 230 | April | 7045 |  |  | 2149 | 222 | Minimum Margin | 1927 | 89.67% | above 1000 MW
20250416 | 330 | April | 7003 |  |  | 2989 | 223 | Minimum Margin | 2766 | 92.54% | above 1000 MW
20250416 | 430 | April | 7003 |  |  | 2989 | 223 | Minimum Margin | 2766 | 92.54% | above 1000 MW
20250416 | 530 | April | 7003 |  |  | 2989 | 223 | Minimum Margin | 2766 | 92.54% | above 1000 MW
20250416 | 630 | April | 6648 |  |  | 2967 | 68 | Minimum Margin | 2899 | 97.71% | above 1000 MW
20250416 | 730 | April | 7315 |  |  | 3420 | 25 | Minimum Margin | 3395 | 99.27% | above 1000 MW
20250416 | 830 | April | 7542 |  |  | 3420 | 252 | Minimum Margin | 3168 | 92.63% | above 1000 MW
20250416 | 930 | April | 7542 |  |  | 1972 | 252 | Minimum Margin | 1720 | 87.22% | above 1000 MW
20250416 | 1030 | April | 7545 |  |  | 1972 | 255 | Minimum Margin | 1717 | 87.07% | above 1000 MW
20250416 | 1130 | April | 7543 |  |  | 1972 | 253 | Minimum Margin | 1719 | 87.17% | above 1000 MW
20250417 | 1830 | April | 7515 |  |  | 2792 | 25 | Minimum Margin | 2767 | 99.1% | above 1000 MW
20250417 | 1930 | April | 7523 |  |  | 2792 | 33 | Minimum Margin | 2759 | 98.82% | above 1000 MW
20250417 | 2030 | April | 7525 |  |  | 2792 | 35 | Minimum Margin | 2757 | 98.75% | above 1000 MW
20250418 | 330 | April | 7006 |  |  | 2400 | 226 | Minimum Margin | 2174 | 90.58% | above 1000 MW
20250418 | 430 | April | 7006 |  |  | 2400 | 226 | Minimum Margin | 2174 | 90.58% | above 1000 MW
20250418 | 530 | April | 7006 |  |  | 2400 | 226 | Minimum Margin | 2174 | 90.58% | above 1000 MW
20250418 | 630 | April | 7006 |  |  | 2400 | 226 | Minimum Margin | 2174 | 90.58% | above 1000 MW
20250418 | 730 | April | 7430 |  |  | 4160 | 240 | Minimum Margin | 3920 | 94.23% | above 1000 MW
20250418 | 830 | April | 7430 |  |  | 4160 | 240 | Minimum Margin | 3920 | 94.23% | above 1000 MW
20250418 | 2130 | April | 8415 |  |  | 1591 | 225 | Minimum Margin | 1366 | 85.86% | above 1000 MW
20250418 | 2230 | April | 8415 |  |  | 1591 | 225 | Minimum Margin | 1366 | 85.86% | above 1000 MW
20250418 | 2330 | April | 7594 |  |  | 1966 | 214 | Minimum Margin | 1752 | 89.11% | above 1000 MW
20250420 | 1830 | April | 7443 |  |  | 3544 | 144 | Minimum Margin | 3400 | 95.94% | above 1000 MW
20250420 | 1930 | April | 7443 |  |  | 3544 | 144 | Minimum Margin | 3400 | 95.94% | above 1000 MW
20250420 | 2030 | April | 7443 |  |  | 3544 | 144 | Minimum Margin | 3400 | 95.94% | above 1000 MW
20250424 | 1830 | April | 4200 |  |  | 6986 | 25 | Minimum Margin | 6961 | 99.64% | above 1000 MW
20250424 | 1930 | April | 4192 |  |  | 6986 | 17 | Minimum Margin | 6969 | 99.76% | above 1000 MW
20250424 | 2030 | April | 4190 |  |  | 6986 | 15 | Minimum Margin | 6971 | 99.79% | above 1000 MW
20250424 | 2130 | April | 6696 |  |  | 2232 | 12 | Minimum Margin | 2220 | 99.46% | above 1000 MW
20250424 | 2230 | April | 6694 |  |  | 2232 | 10 | Minimum Margin | 2222 | 99.55% | above 1000 MW
20250424 | 2330 | April | 6103 |  |  | 2973 | 234 | Minimum Margin | 2739 | 92.13% | above 1000 MW
20250425 | 730 | April | 3168 |  |  | 8204 | 8 | Minimum Margin | 8196 | 99.9% | above 1000 MW
20250425 | 830 | April | 3168 |  |  | 8204 | 8 | Minimum Margin | 8196 | 99.9% | above 1000 MW
20250426 | 30 | April | 7568 |  |  | 2179 | 108 | Minimum Margin | 2071 | 95.04% | above 1000 MW
20250426 | 130 | April | 7568 |  |  | 2179 | 108 | Minimum Margin | 2071 | 95.04% | above 1000 MW
20250426 | 230 | April | 7568 |  |  | 2179 | 108 | Minimum Margin | 2071 | 95.04% | above 1000 MW
20250426 | 330 | April | 7590 |  |  | 1525 | 130 | Minimum Margin | 1395 | 91.48% | above 1000 MW
20250426 | 430 | April | 7657 |  |  | 1525 | 197 | Minimum Margin | 1328 | 87.08% | above 1000 MW
20250426 | 530 | April | 7704 |  |  | 1525 | 244 | Minimum Margin | 1281 | 84% | above 1000 MW
20250426 | 630 | April | 7460 |  |  | 1525 | 0 | TTC Selection - LTTC | 1525 | 100% | above 1000 MW
20250426 | 930 | April | 8175 |  |  | 3371 | 0 | TTC Selection - LTTC | 3371 | 100% | above 1000 MW
20250426 | 1030 | April | 8309 |  |  | 3371 | 134 | Minimum Margin | 3237 | 96.02% | above 1000 MW
20250426 | 1130 | April | 8305 |  |  | 3371 | 130 | Minimum Margin | 3241 | 96.14% | above 1000 MW
20250427 | 2130 | April | 7360 |  |  | 2459 | 0 | TTC Selection - LTTC | 2459 | 100% | above 1000 MW
20250427 | 2230 | April | 7396 |  |  | 2459 | 36 | Minimum Margin | 2423 | 98.54% | above 1000 MW
20250427 | 2330 | April | 7591 |  |  | 2459 | 231 | Minimum Margin | 2228 | 90.61% | above 1000 MW
20250428 | 330 | April | 7592 |  |  | 828 | 132 | Minimum Margin | 696 | 84.06% | [500-1000] MW
20250428 | 430 | April | 7592 |  |  | 828 | 132 | Minimum Margin | 696 | 84.06% | [500-1000] MW
20250428 | 530 | April | 7592 |  |  | 828 | 132 | Minimum Margin | 696 | 84.06% | [500-1000] MW
20250428 | 630 | April | 7497 |  |  | 856 | 237 | Minimum Margin | 619 | 72.31% | [500-1000] MW
20250428 | 730 | April | 6286 |  |  | 2138 | 111 | Minimum Margin | 2027 | 94.81% | above 1000 MW
20250428 | 830 | April | 6348 |  |  | 2138 | 173 | Minimum Margin | 1965 | 91.91% | above 1000 MW
20250428 | 930 | April | 6370 |  |  | 2046 | 195 | Minimum Margin | 1851 | 90.47% | above 1000 MW
20250428 | 1030 | April | 6363 |  |  | 2046 | 188 | Minimum Margin | 1858 | 90.81% | above 1000 MW
20250428 | 1130 | April | 6351 |  |  | 2046 | 176 | Minimum Margin | 1870 | 91.4% | above 1000 MW
20250428 | 1530 | April | 6355 |  |  | 2258 | 180 | Minimum Margin | 2078 | 92.03% | above 1000 MW
20250428 | 1630 | April | 6321 |  |  | 2258 | 146 | Minimum Margin | 2112 | 93.53% | above 1000 MW
20250428 | 1730 | April | 8230 |  |  | 2279 | 255 | Minimum Margin | 2024 | 88.81% | above 1000 MW
20250428 | 2130 | April | 8345 |  |  | 1813 | 170 | Minimum Margin | 1643 | 90.62% | above 1000 MW
20250428 | 2230 | April | 8345 |  |  | 1813 | 170 | Minimum Margin | 1643 | 90.62% | above 1000 MW
20250428 | 2330 | April | 7520 |  |  | 2148 | 160 | Minimum Margin | 1988 | 92.55% | above 1000 MW
20250429 | 30 | April | 7534 |  |  | 174 | 154 | Minimum Margin | 20 | 11.49% | below 500 MW
20250429 | 130 | April | 7534 |  |  | 174 | 154 | Minimum Margin | 20 | 11.49% | below 500 MW
20250429 | 230 | April | 7534 |  |  | 174 | 154 | Minimum Margin | 20 | 11.49% | below 500 MW
20250429 | 730 | April | 8586 |  |  | 1121 | 451 | Minimum Margin | 670 | 59.77% | above 1000 MW
20250429 | 830 | April | 8586 |  |  | 1121 | 451 | Minimum Margin | 670 | 59.77% | above 1000 MW
20250429 | 1830 | April | 7348 |  |  | 3663 | 158 | Minimum Margin | 3505 | 95.69% | above 1000 MW
20250429 | 1930 | April | 7348 |  |  | 3663 | 158 | Minimum Margin | 3505 | 95.69% | above 1000 MW
20250429 | 2030 | April | 7348 |  |  | 3663 | 158 | Minimum Margin | 3505 | 95.69% | above 1000 MW
20250429 | 2130 | April | 7360 |  |  | 2976 | 170 | Minimum Margin | 2806 | 94.29% | above 1000 MW
20250429 | 2230 | April | 7360 |  |  | 2976 | 170 | Minimum Margin | 2806 | 94.29% | above 1000 MW
20250429 | 2330 | April | 6539 |  |  | 3287 | 159 | Minimum Margin | 3128 | 95.16% | above 1000 MW
20250501 | 30 | May |  | 6209 | 559 | 2413 | 116 | Minimum Margin | 2297 | 95.19% | above 1000 MW
20250501 | 130 | May |  | 6209 | 559 | 2413 | 116 | Minimum Margin | 2297 | 95.19% | above 1000 MW
20250501 | 230 | May |  | 6209 | 559 | 2413 | 116 | Minimum Margin | 2297 | 95.19% | above 1000 MW
20250501 | 330 | May |  | 5803 | 395 | 2502 | 116 | Minimum Margin | 2386 | 95.36% | above 1000 MW
20250501 | 430 | May |  | 5803 | 395 | 2502 | 116 | Minimum Margin | 2386 | 95.36% | above 1000 MW
20250501 | 530 | May |  | 5803 | 395 | 2502 | 116 | Minimum Margin | 2386 | 95.36% | above 1000 MW
20250501 | 630 | May |  | 5603 | 395 | 2557 | 116 | Minimum Margin | 2441 | 95.46% | above 1000 MW
20250501 | 730 | May | 6638 |  |  | 3526 | 126 | Minimum Margin | 3400 | 96.43% | above 1000 MW
20250501 | 830 | May | 6683 |  |  | 3526 | 171 | Minimum Margin | 3355 | 95.15% | above 1000 MW
20250501 | 1830 | May |  | 5376 | 638 | 3424 | 107 | Minimum Margin | 3317 | 96.88% | above 1000 MW
20250501 | 1930 | May |  | 5398 | 640 | 3424 | 128 | Minimum Margin | 3296 | 96.26% | above 1000 MW
20250501 | 2030 | May |  | 5449 | 646 | 3424 | 180 | Minimum Margin | 3244 | 94.74% | above 1000 MW
20250501 | 2130 | May |  | 7678 | 717 | 1422 | 51 | Minimum Margin | 1371 | 96.41% | above 1000 MW
20250501 | 2230 | May |  | 7783 | 726 | 1422 | 156 | Minimum Margin | 1266 | 89.03% | above 1000 MW
20250501 | 2330 | May |  | 7758 | 724 | 1422 | 132 | Minimum Margin | 1290 | 90.72% | above 1000 MW
20250502 | 1830 | May |  | 7379 | 769 | 2054 | 88 | Minimum Margin | 1966 | 95.72% | above 1000 MW
20250502 | 1930 | May |  | 7373 | 768 | 2054 | 82 | Minimum Margin | 1972 | 96.01% | above 1000 MW
20250502 | 2030 | May |  | 7371 | 768 | 2054 | 80 | Minimum Margin | 1974 | 96.11% | above 1000 MW
20250505 | 30 | May |  | 6915 | 863 | 76 | 50 | Minimum Margin | 26 | 34.21% | below 500 MW
20250505 | 130 | May |  | 6915 | 863 | 76 | 50 | Minimum Margin | 26 | 34.21% | below 500 MW
20250505 | 230 | May |  | 6915 | 863 | 76 | 50 | Minimum Margin | 26 | 34.21% | below 500 MW
20250505 | 730 | May |  | 6474 | 116 | 4192 | 87 | Minimum Margin | 4105 | 97.92% | above 1000 MW
20250505 | 830 | May |  | 5574 | 116 | 4438 | 87 | Minimum Margin | 4351 | 98.04% | above 1000 MW
20250505 | 930 | May | 5688 |  |  | 3916 | 8 | Minimum Margin | 3908 | 99.8% | above 1000 MW
20250505 | 1030 | May | 5827 |  |  | 3916 | 147 | Minimum Margin | 3769 | 96.25% | above 1000 MW
20250505 | 1130 | May | 5827 |  |  | 3916 | 147 | Minimum Margin | 3769 | 96.25% | above 1000 MW
20250505 | 1230 | May |  | 5040 | 444 | 3204 | 101 | Minimum Margin | 3103 | 96.85% | above 1000 MW
20250505 | 1330 | May |  | 5024 | 442 | 3204 | 85 | Minimum Margin | 3119 | 97.35% | above 1000 MW
20250505 | 1430 | May |  | 5047 | 445 | 3204 | 108 | Minimum Margin | 3096 | 96.63% | above 1000 MW
20250505 | 1530 | May | 5800 |  |  | 4117 | 120 | Minimum Margin | 3997 | 97.09% | above 1000 MW
20250505 | 1630 | May | 5890 |  |  | 4117 | 210 | Minimum Margin | 3907 | 94.9% | above 1000 MW
20250505 | 1730 | May | 5796 |  |  | 4117 | 116 | Minimum Margin | 4001 | 97.18% | above 1000 MW
20250506 | 930 | May | 5876 |  |  | 3798 | 196 | Minimum Margin | 3602 | 94.84% | above 1000 MW
20250506 | 1030 | May | 5882 |  |  | 3798 | 202 | Minimum Margin | 3596 | 94.68% | above 1000 MW
20250506 | 1130 | May | 5835 |  |  | 3798 | 155 | Minimum Margin | 3643 | 95.92% | above 1000 MW
20250506 | 1230 | May | 8034 |  |  | 1295 | 122 | Minimum Margin | 1173 | 90.58% | above 1000 MW
20250506 | 1330 | May | 8034 |  |  | 1295 | 122 | Minimum Margin | 1173 | 90.58% | above 1000 MW
20250506 | 1430 | May | 8034 |  |  | 1295 | 122 | Minimum Margin | 1173 | 90.58% | above 1000 MW
20250506 | 1530 | May | 5797 |  |  | 3647 | 117 | Minimum Margin | 3530 | 96.79% | above 1000 MW
20250506 | 1630 | May | 5839 |  |  | 3647 | 159 | Minimum Margin | 3488 | 95.64% | above 1000 MW
20250506 | 1730 | May | 5870 |  |  | 3647 | 190 | Minimum Margin | 3457 | 94.79% | above 1000 MW
20250506 | 1830 | May |  | 6432 | 594 | 1662 | 154 | Minimum Margin | 1508 | 90.73% | above 1000 MW
20250506 | 1930 | May |  | 6370 | 588 | 1662 | 92 | Minimum Margin | 1570 | 94.46% | above 1000 MW
20250506 | 2030 | May |  | 6414 | 592 | 1662 | 136 | Minimum Margin | 1526 | 91.82% | above 1000 MW
20250507 | 1230 | May | 5746 |  |  | 2761 | 126 | Minimum Margin | 2635 | 95.44% | above 1000 MW
20250507 | 1330 | May | 5746 |  |  | 2761 | 126 | Minimum Margin | 2635 | 95.44% | above 1000 MW
20250507 | 1430 | May | 5746 |  |  | 2761 | 126 | Minimum Margin | 2635 | 95.44% | above 1000 MW
20250507 | 1530 | May |  | 5326 | 337 | 2382 | 119 | Minimum Margin | 2263 | 95% | above 1000 MW
20250507 | 1630 | May |  | 5386 | 337 | 2355 | 119 | Minimum Margin | 2236 | 94.95% | above 1000 MW
20250507 | 1730 | May |  | 5386 | 337 | 2355 | 119 | Minimum Margin | 2236 | 94.95% | above 1000 MW
20250507 | 1830 | May |  | 6237 | 587 | 2602 | 396 | Minimum Margin | 2206 | 84.78% | above 1000 MW
20250507 | 1930 | May |  | 6087 | 573 | 2602 | 246 | Minimum Margin | 2356 | 90.55% | above 1000 MW
20250507 | 2030 | May |  | 5913 | 558 | 2602 | 72 | Minimum Margin | 2530 | 97.23% | above 1000 MW
20250507 | 2130 | May |  | 7106 | 690 | 1946 | 335 | Minimum Margin | 1611 | 82.79% | above 1000 MW
20250507 | 2230 | May |  | 7164 | 695 | 1946 | 393 | Minimum Margin | 1553 | 79.8% | above 1000 MW
20250507 | 2330 | May |  | 6584 | 720 | 2495 | 393 | Minimum Margin | 2102 | 84.25% | above 1000 MW
20250508 | 30 | May |  | 7777 | 727 | 2163 | 162 | Minimum Margin | 2001 | 92.51% | above 1000 MW
20250508 | 130 | May |  | 7777 | 727 | 2163 | 162 | Minimum Margin | 2001 | 92.51% | above 1000 MW
20250508 | 230 | May |  | 7777 | 727 | 2163 | 162 | Minimum Margin | 2001 | 92.51% | above 1000 MW
20250508 | 930 | May | 6799 |  |  | 3249 | 219 | Minimum Margin | 3030 | 93.26% | above 1000 MW
20250508 | 1030 | May | 6740 |  |  | 3249 | 160 | Minimum Margin | 3089 | 95.08% | above 1000 MW
20250508 | 1130 | May | 6740 |  |  | 3249 | 160 | Minimum Margin | 3089 | 95.08% | above 1000 MW
20250508 | 1230 | May | 6741 |  |  | 4029 | 161 | Minimum Margin | 3868 | 96% | above 1000 MW
20250508 | 1330 | May | 6741 |  |  | 4029 | 161 | Minimum Margin | 3868 | 96% | above 1000 MW
20250508 | 1430 | May | 6741 |  |  | 4029 | 161 | Minimum Margin | 3868 | 96% | above 1000 MW
20250508 | 1530 | May | 6743 |  |  | 3332 | 163 | Minimum Margin | 3169 | 95.11% | above 1000 MW
20250508 | 1630 | May | 6739 |  |  | 3332 | 159 | Minimum Margin | 3173 | 95.23% | above 1000 MW
20250508 | 1730 | May | 6739 |  |  | 3332 | 159 | Minimum Margin | 3173 | 95.23% | above 1000 MW
20250509 | 730 | May |  | 7164 | 594 | 1295 | 0 | Critical Branch | 1295 | 100% | above 1000 MW
20250509 | 830 | May |  | 7316 | 606 | 1295 | 152 | Minimum Margin | 1143 | 88.26% | above 1000 MW
20250509 | 930 | May | 7665 |  |  | 5361 | 213 | Minimum Margin | 5148 | 96.03% | above 1000 MW
20250509 | 1030 | May | 7619 |  |  | 5361 | 167 | Minimum Margin | 5194 | 96.88% | above 1000 MW
20250509 | 1130 | May | 7603 |  |  | 5361 | 151 | Minimum Margin | 5210 | 97.18% | above 1000 MW
20250509 | 1530 | May |  | 8035 | 646 | 3037 | 132 | Minimum Margin | 2905 | 95.65% | above 1000 MW
20250509 | 1630 | May |  | 8035 | 646 | 3037 | 132 | Minimum Margin | 2905 | 95.65% | above 1000 MW
20250509 | 1730 | May |  | 8165 | 646 | 2965 | 132 | Minimum Margin | 2833 | 95.55% | above 1000 MW
20250511 | 330 | May |  | 3641 | 2109 | 1179 | 109 | Minimum Margin | 1070 | 90.75% | above 1000 MW
20250511 | 430 | May |  | 3641 | 2109 | 1179 | 109 | Minimum Margin | 1070 | 90.75% | above 1000 MW
20250511 | 530 | May |  | 3641 | 2109 | 1179 | 109 | Minimum Margin | 1070 | 90.75% | above 1000 MW
20250511 | 630 | May |  | 3641 | 2109 | 1179 | 109 | Minimum Margin | 1070 | 90.75% | above 1000 MW
20250511 | 1830 | May |  | 7351 | 663 | 1319 | 8 | Minimum Margin | 1311 | 99.39% | above 1000 MW
20250511 | 1930 | May |  | 7353 | 663 | 1319 | 10 | Minimum Margin | 1309 | 99.24% | above 1000 MW
20250511 | 2030 | May |  | 7353 | 663 | 1319 | 10 | Minimum Margin | 1309 | 99.24% | above 1000 MW
20250512 | 1830 | May | 6306 |  |  | 5135 | 26 | Minimum Margin | 5109 | 99.49% | above 1000 MW
20250512 | 1930 | May | 6289 |  |  | 5135 | 9 | Minimum Margin | 5126 | 99.82% | above 1000 MW
20250512 | 2030 | May | 6291 |  |  | 5135 | 11 | Minimum Margin | 5124 | 99.79% | above 1000 MW
20250512 | 2130 | May | 7869 |  |  | 5707 | 9 | Minimum Margin | 5698 | 99.84% | above 1000 MW
20250512 | 2230 | May | 7867 |  |  | 5707 | 7 | Minimum Margin | 5700 | 99.88% | above 1000 MW
20250512 | 2330 | May | 7422 |  |  | 6037 | 162 | Minimum Margin | 5875 | 97.32% | above 1000 MW
20250513 | 30 | May | 5891 |  |  | 2714 | 111 | Minimum Margin | 2603 | 95.91% | above 1000 MW
20250513 | 130 | May | 5891 |  |  | 2714 | 111 | Minimum Margin | 2603 | 95.91% | above 1000 MW
20250513 | 230 | May | 5891 |  |  | 2714 | 111 | Minimum Margin | 2603 | 95.91% | above 1000 MW
20250513 | 330 | May |  | 5506 | 394 | 1427 | 114 | Minimum Margin | 1313 | 92.01% | above 1000 MW
20250513 | 430 | May |  | 5506 | 394 | 1427 | 114 | Minimum Margin | 1313 | 92.01% | above 1000 MW
20250513 | 530 | May |  | 5506 | 394 | 1427 | 114 | Minimum Margin | 1313 | 92.01% | above 1000 MW
20250513 | 630 | May |  | 5349 | 398 | 1485 | 157 | Minimum Margin | 1328 | 89.43% | above 1000 MW
20250513 | 730 | May | 6380 |  |  | 6148 | 214 | Minimum Margin | 5934 | 96.52% | above 1000 MW
20250513 | 830 | May | 6383 |  |  | 6148 | 217 | Minimum Margin | 5931 | 96.47% | above 1000 MW
20250513 | 1230 | May | 6279 |  |  | 4525 | 149 | Minimum Margin | 4376 | 96.71% | above 1000 MW
20250513 | 1330 | May | 6280 |  |  | 4525 | 150 | Minimum Margin | 4375 | 96.69% | above 1000 MW
20250513 | 1430 | May | 6279 |  |  | 4525 | 149 | Minimum Margin | 4376 | 96.71% | above 1000 MW
20250513 | 1530 | May | 6283 |  |  | 2698 | 153 | Minimum Margin | 2545 | 94.33% | above 1000 MW
20250513 | 1630 | May | 6283 |  |  | 2698 | 153 | Minimum Margin | 2545 | 94.33% | above 1000 MW
20250513 | 1730 | May | 6283 |  |  | 2698 | 153 | Minimum Margin | 2545 | 94.33% | above 1000 MW
20250513 | 1830 | May | 6683 |  |  | 2597 | 403 | Minimum Margin | 2194 | 84.48% | above 1000 MW
20250513 | 1930 | May | 6683 |  |  | 2597 | 403 | Minimum Margin | 2194 | 84.48% | above 1000 MW
20250513 | 2030 | May | 6459 |  |  | 2597 | 179 | Minimum Margin | 2418 | 93.11% | above 1000 MW
20250513 | 2130 | May | 6680 |  |  | 3535 | 400 | Minimum Margin | 3135 | 88.68% | above 1000 MW
20250513 | 2230 | May | 6680 |  |  | 3535 | 400 | Minimum Margin | 3135 | 88.68% | above 1000 MW
20250513 | 2330 | May | 6078 |  |  | 4075 | 398 | Minimum Margin | 3677 | 90.23% | above 1000 MW
20250514 | 730 | May | 6280 |  |  | 6133 | 0 | TTC Selection - LTTC | 6133 | 100% | above 1000 MW
20250514 | 830 | May | 6280 |  |  | 6133 | 0 | TTC Selection - LTTC | 6133 | 100% | above 1000 MW
20250514 | 930 | May | 8125 |  |  | 2267 | 176 | Minimum Margin | 2091 | 92.24% | above 1000 MW
20250514 | 1030 | May | 8106 |  |  | 2267 | 157 | Minimum Margin | 2110 | 93.07% | above 1000 MW
20250514 | 1130 | May | 8106 |  |  | 2267 | 157 | Minimum Margin | 2110 | 93.07% | above 1000 MW
20250514 | 1830 | May |  | 6010 | 418 | 1705 | 152 | Minimum Margin | 1553 | 91.09% | above 1000 MW
20250514 | 1930 | May |  | 5858 | 405 | 1705 | 0 | TTC Selection - LTTCImport | 1705 | 100% | above 1000 MW
20250514 | 2030 | May |  | 5991 | 416 | 1705 | 133 | Minimum Margin | 1572 | 92.2% | above 1000 MW
20250514 | 2130 | May |  | 5944 | 449 | 1972 | 86 | Minimum Margin | 1886 | 95.64% | above 1000 MW
20250514 | 2230 | May |  | 6282 | 477 | 1972 | 423 | Minimum Margin | 1549 | 78.55% | above 1000 MW
20250514 | 2330 | May |  | 5438 | 479 | 2538 | 140 | Minimum Margin | 2398 | 94.48% | above 1000 MW
20250515 | 30 | May |  | 6247 | 588 | 900 | 454 | Minimum Margin | 446 | 49.56% | [500-1000] MW
20250515 | 130 | May |  | 6247 | 588 | 900 | 454 | Minimum Margin | 446 | 49.56% | [500-1000] MW
20250515 | 230 | May |  | 6247 | 588 | 900 | 454 | Minimum Margin | 446 | 49.56% | [500-1000] MW
20250515 | 330 | May |  | 5507 | 503 | 2334 | 116 | Minimum Margin | 2218 | 95.03% | above 1000 MW
20250515 | 430 | May |  | 5507 | 503 | 2334 | 116 | Minimum Margin | 2218 | 95.03% | above 1000 MW
20250515 | 530 | May |  | 5507 | 503 | 2334 | 116 | Minimum Margin | 2218 | 95.03% | above 1000 MW
20250515 | 630 | May |  | 5507 | 503 | 2334 | 116 | Minimum Margin | 2218 | 95.03% | above 1000 MW
20250515 | 730 | May | 6712 |  |  | 1698 | 432 | Minimum Margin | 1266 | 74.56% | above 1000 MW
20250515 | 830 | May | 6626 |  |  | 1698 | 346 | Minimum Margin | 1352 | 79.62% | above 1000 MW
20250515 | 930 | May | 6454 |  |  | 4420 | 174 | Minimum Margin | 4246 | 96.06% | above 1000 MW
20250515 | 1030 | May | 6437 |  |  | 4420 | 157 | Minimum Margin | 4263 | 96.45% | above 1000 MW
20250515 | 1130 | May | 6437 |  |  | 4420 | 157 | Minimum Margin | 4263 | 96.45% | above 1000 MW
20250515 | 1830 | May | 6444 |  |  | 3623 | 164 | Minimum Margin | 3459 | 95.47% | above 1000 MW
20250515 | 1930 | May | 6444 |  |  | 3623 | 164 | Minimum Margin | 3459 | 95.47% | above 1000 MW
20250515 | 2030 | May | 6444 |  |  | 3623 | 164 | Minimum Margin | 3459 | 95.47% | above 1000 MW
20250515 | 2130 | May | 6650 |  |  | 1187 | 370 | Minimum Margin | 817 | 68.83% | above 1000 MW
20250515 | 2230 | May | 6595 |  |  | 1187 | 315 | Minimum Margin | 872 | 73.46% | above 1000 MW
20250515 | 2330 | May | 6114 |  |  | 1757 | 434 | Minimum Margin | 1323 | 75.3% | above 1000 MW
20250516 | 30 | May | 6914 |  |  | 2091 | 128 | Minimum Margin | 1963 | 93.88% | above 1000 MW
20250516 | 130 | May | 6931 |  |  | 2091 | 145 | Minimum Margin | 1946 | 93.07% | above 1000 MW
20250516 | 230 | May | 6931 |  |  | 2091 | 145 | Minimum Margin | 1946 | 93.07% | above 1000 MW
20250516 | 330 | May |  | 5535 | 482 | 2132 | 144 | Minimum Margin | 1988 | 93.25% | above 1000 MW
20250516 | 430 | May |  | 5535 | 482 | 2132 | 144 | Minimum Margin | 1988 | 93.25% | above 1000 MW
20250516 | 530 | May |  | 5535 | 482 | 2132 | 144 | Minimum Margin | 1988 | 93.25% | above 1000 MW
20250516 | 630 | May |  | 5554 | 483 | 2132 | 163 | Minimum Margin | 1969 | 92.35% | above 1000 MW
20250516 | 930 | May | 6426 |  |  | 2855 | 146 | Minimum Margin | 2709 | 94.89% | above 1000 MW
20250516 | 1030 | May | 6426 |  |  | 2855 | 146 | Minimum Margin | 2709 | 94.89% | above 1000 MW
20250516 | 1130 | May | 6426 |  |  | 2855 | 146 | Minimum Margin | 2709 | 94.89% | above 1000 MW
20250516 | 1230 | May | 7926 |  |  | 3769 | 143 | Minimum Margin | 3626 | 96.21% | above 1000 MW
20250516 | 1330 | May | 7926 |  |  | 3769 | 143 | Minimum Margin | 3626 | 96.21% | above 1000 MW
20250516 | 1430 | May | 7926 |  |  | 3769 | 143 | Minimum Margin | 3626 | 96.21% | above 1000 MW
20250516 | 1530 | May | 6416 |  |  | 3497 | 136 | Minimum Margin | 3361 | 96.11% | above 1000 MW
20250516 | 1630 | May | 6416 |  |  | 3497 | 136 | Minimum Margin | 3361 | 96.11% | above 1000 MW
20250516 | 1730 | May | 6723 |  |  | 3547 | 143 | Minimum Margin | 3404 | 95.97% | above 1000 MW
20250516 | 1830 | May | 6743 |  |  | 3993 | 163 | Minimum Margin | 3830 | 95.92% | above 1000 MW
20250516 | 1930 | May | 6743 |  |  | 3993 | 163 | Minimum Margin | 3830 | 95.92% | above 1000 MW
20250516 | 2030 | May | 6743 |  |  | 3993 | 163 | Minimum Margin | 3830 | 95.92% | above 1000 MW
20250517 | 30 | May |  | 5888 | 426 | 1412 | 201 | Minimum Margin | 1211 | 85.76% | above 1000 MW
20250517 | 130 | May |  | 5885 | 426 | 1412 | 197 | Minimum Margin | 1215 | 86.05% | above 1000 MW
20250517 | 230 | May |  | 5859 | 423 | 1412 | 172 | Minimum Margin | 1240 | 87.82% | above 1000 MW
20250517 | 930 | May |  | 6362 | 400 | 3346 | 208 | Minimum Margin | 3138 | 93.78% | above 1000 MW
20250517 | 1030 | May |  | 6298 | 395 | 3346 | 143 | Minimum Margin | 3203 | 95.73% | above 1000 MW
20250517 | 1130 | May |  | 6298 | 395 | 3346 | 143 | Minimum Margin | 3203 | 95.73% | above 1000 MW
20250517 | 1530 | May | 6788 |  |  | 5936 | 208 | Minimum Margin | 5728 | 96.5% | above 1000 MW
20250517 | 1630 | May | 6785 |  |  | 5936 | 205 | Minimum Margin | 5731 | 96.55% | above 1000 MW
20250517 | 1730 | May | 6739 |  |  | 5936 | 159 | Minimum Margin | 5777 | 97.32% | above 1000 MW
20250517 | 1830 | May | 6738 |  |  | 1866 | 158 | Minimum Margin | 1708 | 91.53% | above 1000 MW
20250517 | 1930 | May | 6789 |  |  | 1866 | 209 | Minimum Margin | 1657 | 88.8% | above 1000 MW
20250517 | 2030 | May | 6580 |  |  | 1866 | 0 | TTC Selection - LTTC | 1866 | 100% | above 1000 MW
20250517 | 2130 | May |  | 6289 | 389 | 2666 | 135 | Minimum Margin | 2531 | 94.94% | above 1000 MW
20250517 | 2230 | May |  | 6289 | 389 | 2666 | 135 | Minimum Margin | 2531 | 94.94% | above 1000 MW
20250517 | 2330 | May |  | 5729 | 414 | 3118 | 135 | Minimum Margin | 2983 | 95.67% | above 1000 MW
20250519 | 30 | May |  | 5743 | 464 | 1402 | 55 | Minimum Margin | 1347 | 96.08% | above 1000 MW
20250519 | 130 | May |  | 5743 | 464 | 1402 | 55 | Minimum Margin | 1347 | 96.08% | above 1000 MW
20250519 | 230 | May |  | 5743 | 464 | 1402 | 55 | Minimum Margin | 1347 | 96.08% | above 1000 MW
20250519 | 330 | May |  | 5816 | 394 | 1899 | 129 | Minimum Margin | 1770 | 93.21% | above 1000 MW
20250519 | 430 | May |  | 5816 | 394 | 1899 | 129 | Minimum Margin | 1770 | 93.21% | above 1000 MW
20250519 | 530 | May |  | 5816 | 394 | 1899 | 129 | Minimum Margin | 1770 | 93.21% | above 1000 MW
20250519 | 630 | May |  | 5816 | 394 | 1899 | 129 | Minimum Margin | 1770 | 93.21% | above 1000 MW
20250519 | 730 | May | 6393 |  |  | 5708 | 113 | Minimum Margin | 5595 | 98.02% | above 1000 MW
20250519 | 830 | May | 6512 |  |  | 5708 | 232 | Minimum Margin | 5476 | 95.94% | above 1000 MW
20250519 | 1230 | May | 6446 |  |  | 6550 | 166 | Minimum Margin | 6384 | 97.47% | above 1000 MW
20250519 | 1330 | May | 6446 |  |  | 6550 | 166 | Minimum Margin | 6384 | 97.47% | above 1000 MW
20250519 | 1430 | May | 6446 |  |  | 6550 | 166 | Minimum Margin | 6384 | 97.47% | above 1000 MW
20250520 | 330 | May |  | 5553 | 398 | 2250 | 162 | Minimum Margin | 2088 | 92.8% | above 1000 MW
20250520 | 430 | May |  | 5492 | 393 | 2250 | 100 | Minimum Margin | 2150 | 95.56% | above 1000 MW
20250520 | 530 | May |  | 5409 | 385 | 2250 | 17 | Minimum Margin | 2233 | 99.24% | above 1000 MW
20250520 | 630 | May |  | 5407 | 385 | 2250 | 15 | Minimum Margin | 2235 | 99.33% | above 1000 MW
20250520 | 1230 | May | 6294 |  |  | 3967 | 164 | Minimum Margin | 3803 | 95.87% | above 1000 MW
20250520 | 1330 | May | 6294 |  |  | 3967 | 164 | Minimum Margin | 3803 | 95.87% | above 1000 MW
20250520 | 1430 | May | 6314 |  |  | 3967 | 184 | Minimum Margin | 3783 | 95.36% | above 1000 MW
20250520 | 1830 | May | 6148 |  |  | 6651 | 18 | Minimum Margin | 6633 | 99.73% | above 1000 MW
20250520 | 1930 | May | 6297 |  |  | 6737 | 17 | Minimum Margin | 6720 | 99.75% | above 1000 MW
20250520 | 2030 | May | 6297 |  |  | 6737 | 17 | Minimum Margin | 6720 | 99.75% | above 1000 MW
20250523 | 30 | May |  | 5541 | 397 | 3341 | 150 | Minimum Margin | 3191 | 95.51% | above 1000 MW
20250523 | 130 | May |  | 5541 | 397 | 3341 | 150 | Minimum Margin | 3191 | 95.51% | above 1000 MW
20250523 | 230 | May |  | 5541 | 397 | 3341 | 150 | Minimum Margin | 3191 | 95.51% | above 1000 MW
20250523 | 330 | May |  | 5542 | 447 | 3095 | 150 | Minimum Margin | 2945 | 95.15% | above 1000 MW
20250523 | 430 | May |  | 5542 | 447 | 3095 | 150 | Minimum Margin | 2945 | 95.15% | above 1000 MW
20250523 | 530 | May |  | 5542 | 447 | 3095 | 150 | Minimum Margin | 2945 | 95.15% | above 1000 MW
20250523 | 630 | May |  | 5546 | 448 | 3095 | 154 | Minimum Margin | 2941 | 95.02% | above 1000 MW
20250523 | 2130 | May |  | 6303 | 441 | 5105 | 149 | Minimum Margin | 4956 | 97.08% | above 1000 MW
20250523 | 2230 | May |  | 6303 | 441 | 5105 | 149 | Minimum Margin | 4956 | 97.08% | above 1000 MW
20250523 | 2330 | May |  | 5743 | 466 | 5564 | 149 | Minimum Margin | 5415 | 97.32% | above 1000 MW
20250524 | 30 | May | 6085 |  |  | 2012 | 5 | Minimum Margin | 2007 | 99.75% | above 1000 MW
20250524 | 130 | May | 6104 |  |  | 2012 | 24 | Minimum Margin | 1988 | 98.81% | above 1000 MW
20250524 | 230 | May | 6264 |  |  | 2012 | 184 | Minimum Margin | 1828 | 90.85% | above 1000 MW
20250524 | 330 | May | 6241 |  |  | 1697 | 161 | Minimum Margin | 1536 | 90.51% | above 1000 MW
20250524 | 430 | May | 6241 |  |  | 1697 | 161 | Minimum Margin | 1536 | 90.51% | above 1000 MW
20250524 | 530 | May | 6283 |  |  | 1697 | 203 | Minimum Margin | 1494 | 88.04% | above 1000 MW
20250524 | 630 | May | 6080 |  |  | 1697 | 0 | TTC Selection - LTTC | 1697 | 100% | above 1000 MW
20250524 | 730 | May |  | 6340 | 494 | 1126 | 186 | Minimum Margin | 940 | 83.48% | above 1000 MW
20250524 | 830 | May |  | 6226 | 485 | 1126 | 72 | Minimum Margin | 1054 | 93.61% | above 1000 MW
20250524 | 930 | May | 7952 |  |  | 3421 | 74 | Minimum Margin | 3347 | 97.84% | above 1000 MW
20250524 | 1030 | May | 8026 |  |  | 3421 | 148 | Minimum Margin | 3273 | 95.67% | above 1000 MW
20250524 | 1130 | May | 8026 |  |  | 3421 | 148 | Minimum Margin | 3273 | 95.67% | above 1000 MW
20250524 | 1530 | May | 6795 |  |  | 4432 | 215 | Minimum Margin | 4217 | 95.15% | above 1000 MW
20250524 | 1630 | May | 6728 |  |  | 4432 | 148 | Minimum Margin | 4284 | 96.66% | above 1000 MW
20250524 | 1730 | May | 6737 |  |  | 4432 | 157 | Minimum Margin | 4275 | 96.46% | above 1000 MW
20250524 | 1830 | May | 6580 |  |  | 1804 | 0 | TTC Selection - LTTC | 1804 | 100% | above 1000 MW
20250524 | 1930 | May | 6809 |  |  | 1804 | 229 | Minimum Margin | 1575 | 87.31% | above 1000 MW
20250524 | 2030 | May | 6580 |  |  | 1804 | 0 | TTC Selection - LTTC | 1804 | 100% | above 1000 MW
20250526 | 730 | May | 5630 |  |  | 3569 | 0 | TTC Selection - LTTC | 3569 | 100% | above 1000 MW
20250526 | 830 | May | 5630 |  |  | 3569 | 0 | TTC Selection - LTTC | 3569 | 100% | above 1000 MW
20250526 | 1230 | May | 5789 |  |  | 2449 | 159 | Minimum Margin | 2290 | 93.51% | above 1000 MW
20250526 | 1330 | May | 5789 |  |  | 2449 | 159 | Minimum Margin | 2290 | 93.51% | above 1000 MW
20250526 | 1430 | May | 5799 |  |  | 2449 | 169 | Minimum Margin | 2280 | 93.1% | above 1000 MW
20250526 | 1530 | May |  | 5370 | 340 | 728 | 152 | Minimum Margin | 576 | 79.12% | [500-1000] MW
20250526 | 1630 | May |  | 5392 | 342 | 728 | 174 | Minimum Margin | 554 | 76.1% | [500-1000] MW
20250526 | 1730 | May |  | 5304 | 334 | 728 | 86 | Minimum Margin | 642 | 88.19% | [500-1000] MW
20250526 | 1830 | May | 5984 |  |  | 1780 | 204 | Minimum Margin | 1576 | 88.54% | above 1000 MW
20250526 | 1930 | May | 5780 |  |  | 1780 | 0 | TTC Selection - LTTC | 1780 | 100% | above 1000 MW
20250526 | 2030 | May | 5832 |  |  | 1780 | 52 | Minimum Margin | 1728 | 97.08% | above 1000 MW
20250526 | 2130 | May |  | 5495 | 441 | 2513 | 129 | Minimum Margin | 2384 | 94.87% | above 1000 MW
20250526 | 2230 | May |  | 5532 | 444 | 2513 | 167 | Minimum Margin | 2346 | 93.35% | above 1000 MW
20250526 | 2330 | May |  | 5191 | 471 | 2875 | 185 | Minimum Margin | 2690 | 93.57% | above 1000 MW
20250527 | 30 | May | 7581 |  |  | 1426 | 139 | Minimum Margin | 1287 | 90.25% | above 1000 MW
20250527 | 130 | May | 7778 |  |  | 1426 | 336 | Minimum Margin | 1090 | 76.44% | above 1000 MW
20250527 | 230 | May | 7630 |  |  | 1426 | 188 | Minimum Margin | 1238 | 86.82% | above 1000 MW
20250527 | 730 | May | 7646 |  |  | 1046 | 0 | Critical Branch | 1046 | 100% | above 1000 MW
20250527 | 830 | May | 7647 |  |  | 1046 | 1 | Minimum Margin | 1045 | 99.9% | above 1000 MW
20250527 | 1530 | May | 6759 |  |  | 1722 | 2 | Minimum Margin | 1720 | 99.88% | above 1000 MW
20250527 | 1630 | May | 6759 |  |  | 1722 | 2 | Minimum Margin | 1720 | 99.88% | above 1000 MW
20250527 | 1730 | May | 6870 |  |  | 1722 | 113 | Minimum Margin | 1609 | 93.44% | above 1000 MW
20250527 | 2130 | May |  | 6667 | 597 | 984 | 126 | Minimum Margin | 858 | 87.2% | [500-1000] MW
20250527 | 2230 | May |  | 6568 | 588 | 984 | 27 | Minimum Margin | 957 | 97.26% | [500-1000] MW
20250527 | 2330 | May |  | 6196 | 612 | 1398 | 15 | Minimum Margin | 1383 | 98.93% | above 1000 MW
20250530 | 930 | May | 6167 |  |  | 2131 | 87 | Minimum Margin | 2044 | 95.92% | above 1000 MW
20250530 | 1030 | May | 6297 |  |  | 2131 | 217 | Minimum Margin | 1914 | 89.82% | above 1000 MW
20250530 | 1130 | May | 6293 |  |  | 2131 | 213 | Minimum Margin | 1918 | 90% | above 1000 MW
20250530 | 1230 | May | 6232 |  |  | 2621 | 152 | Minimum Margin | 2469 | 94.2% | above 1000 MW
20250530 | 1330 | May | 6263 |  |  | 2621 | 183 | Minimum Margin | 2438 | 93.02% | above 1000 MW
20250530 | 1430 | May | 6246 |  |  | 2621 | 166 | Minimum Margin | 2455 | 93.67% | above 1000 MW
20250530 | 1530 | May |  | 5835 | 387 | 1967 | 174 | Minimum Margin | 1793 | 91.15% | above 1000 MW
20250530 | 1630 | May |  | 5790 | 383 | 1967 | 129 | Minimum Margin | 1838 | 93.44% | above 1000 MW
20250530 | 1730 | May |  | 5830 | 386 | 1967 | 169 | Minimum Margin | 1798 | 91.41% | above 1000 MW
20250530 | 1830 | May |  | 6753 | 580 | 2195 | 37 | Minimum Margin | 2158 | 98.31% | above 1000 MW
20250530 | 1930 | May |  | 6909 | 594 | 2195 | 193 | Minimum Margin | 2002 | 91.21% | above 1000 MW
20250530 | 2030 | May |  | 6901 | 593 | 2195 | 185 | Minimum Margin | 2010 | 91.57% | above 1000 MW
20250531 | 330 | May | 6129 |  |  | 26 | 0 | Critical Branch | 26 | 100% | below 500 MW
20250531 | 630 | May | 6130 |  |  | 26 | 1 | Minimum Margin | 25 | 96.15% | below 500 MW
20250531 | 1830 | May |  | 6468 | 555 | 2276 | 2 | Minimum Margin | 2274 | 99.91% | above 1000 MW
20250531 | 1930 | May |  | 6468 | 555 | 2276 | 2 | Minimum Margin | 2274 | 99.91% | above 1000 MW
20250531 | 2030 | May |  | 6468 | 555 | 2276 | 2 | Minimum Margin | 2274 | 99.91% | above 1000 MW
20250601 | 730 | June |  | 7564 | 975 | 385 | 323 | Minimum Margin | 62 | 16.1% | below 500 MW
20250601 | 830 | June |  | 7613 | 981 | 385 | 372 | Minimum Margin | 13 | 3.377% | below 500 MW
20250602 | 30 | June |  | 8205 | 1031 | 395 | 64 | Minimum Margin | 331 | 83.8% | below 500 MW
20250602 | 130 | June |  | 8205 | 1031 | 395 | 64 | Minimum Margin | 331 | 83.8% | below 500 MW
20250602 | 230 | June |  | 8205 | 1031 | 395 | 64 | Minimum Margin | 331 | 83.8% | below 500 MW
20250602 | 330 | June |  | 7418 | 697 | 1232 | 0 | Critical Branch | 1232 | 100% | above 1000 MW
20250602 | 430 | June |  | 7418 | 697 | 1232 | 0 | Critical Branch | 1232 | 100% | above 1000 MW
20250602 | 530 | June |  | 7418 | 697 | 1232 | 0 | Critical Branch | 1232 | 100% | above 1000 MW
20250602 | 630 | June |  | 7418 | 697 | 1232 | 0 | Critical Branch | 1232 | 100% | above 1000 MW
20250602 | 930 | June | 5815 |  |  | 4529 | 135 | Minimum Margin | 4394 | 97.02% | above 1000 MW
20250602 | 1030 | June | 5815 |  |  | 4529 | 135 | Minimum Margin | 4394 | 97.02% | above 1000 MW
20250602 | 1130 | June | 5823 |  |  | 4529 | 143 | Minimum Margin | 4386 | 96.84% | above 1000 MW
20250602 | 1830 | June |  | 6793 | 639 | 3875 | 0 | Critical Branch | 3875 | 100% | above 1000 MW
20250602 | 1930 | June |  | 6793 | 639 | 3875 | 0 | Critical Branch | 3875 | 100% | above 1000 MW
20250602 | 2030 | June |  | 6793 | 639 | 3875 | 0 | Critical Branch | 3875 | 100% | above 1000 MW
20250603 | 930 | June | 6455 |  |  | 2421 | 0 | Critical Branch | 2421 | 100% | above 1000 MW
20250603 | 1030 | June | 6585 |  |  | 2421 | 130 | Minimum Margin | 2291 | 94.63% | above 1000 MW
20250603 | 1130 | June | 6654 |  |  | 2421 | 199 | Minimum Margin | 2222 | 91.78% | above 1000 MW
20250603 | 1230 | June | 7145 |  |  | 2804 | 170 | Minimum Margin | 2634 | 93.94% | above 1000 MW
20250603 | 1330 | June | 7145 |  |  | 2804 | 170 | Minimum Margin | 2634 | 93.94% | above 1000 MW
20250603 | 1430 | June | 7145 |  |  | 2804 | 170 | Minimum Margin | 2634 | 93.94% | above 1000 MW
20250603 | 1530 | June | 6541 |  |  | 2258 | 189 | Minimum Margin | 2069 | 91.63% | above 1000 MW
20250603 | 1630 | June | 6554 |  |  | 2258 | 202 | Minimum Margin | 2056 | 91.05% | above 1000 MW
20250603 | 1730 | June | 6352 |  |  | 2258 | 0 | Critical Branch | 2258 | 100% | above 1000 MW
20250604 | 930 | June | 5232 |  |  | 3701 | 2 | Minimum Margin | 3699 | 99.95% | above 1000 MW
20250604 | 1030 | June | 5463 |  |  | 3701 | 233 | Minimum Margin | 3468 | 93.7% | above 1000 MW
20250604 | 1130 | June | 5232 |  |  | 3701 | 2 | Minimum Margin | 3699 | 99.95% | above 1000 MW
20250605 | 730 | June | 6960 |  |  | 5101 | 19 | Minimum Margin | 5082 | 99.63% | above 1000 MW
20250605 | 830 | June | 6958 |  |  | 5101 | 17 | Minimum Margin | 5084 | 99.67% | above 1000 MW
20250605 | 930 | June | 5245 |  |  | 4149 | 15 | Minimum Margin | 4134 | 99.64% | above 1000 MW
20250605 | 1030 | June | 5452 |  |  | 4149 | 222 | Minimum Margin | 3927 | 94.65% | above 1000 MW
20250605 | 1130 | June | 5438 |  |  | 4149 | 208 | Minimum Margin | 3941 | 94.99% | above 1000 MW
20250605 | 1230 | June | 5437 |  |  | 3669 | 207 | Minimum Margin | 3462 | 94.36% | above 1000 MW
20250605 | 1330 | June | 5437 |  |  | 3669 | 207 | Minimum Margin | 3462 | 94.36% | above 1000 MW
20250605 | 1430 | June | 5439 |  |  | 3669 | 209 | Minimum Margin | 3460 | 94.3% | above 1000 MW
20250605 | 1530 | June | 5234 |  |  | 3776 | 4 | Minimum Margin | 3772 | 99.89% | above 1000 MW
20250605 | 1630 | June | 5241 |  |  | 3776 | 11 | Minimum Margin | 3765 | 99.71% | above 1000 MW
20250605 | 1730 | June | 5942 |  |  | 2297 | 12 | Minimum Margin | 2285 | 99.48% | above 1000 MW
20250606 | 730 | June | 7267 |  |  | 2266 | 0 | Critical Branch | 2266 | 100% | above 1000 MW
20250606 | 830 | June | 7267 |  |  | 2266 | 0 | Critical Branch | 2266 | 100% | above 1000 MW
20250606 | 930 | June | 5953 |  |  | 3218 | 23 | Minimum Margin | 3195 | 99.29% | above 1000 MW
20250606 | 1030 | June | 6002 |  |  | 3218 | 72 | Minimum Margin | 3146 | 97.76% | above 1000 MW
20250606 | 1130 | June | 5930 |  |  | 3218 | 0 | TTC Selection - LTTC | 3218 | 100% | above 1000 MW
20250606 | 1830 | June |  | 6202 | 532 | 4574 | 111 | Minimum Margin | 4463 | 97.57% | above 1000 MW
20250606 | 1930 | June |  | 6205 | 533 | 4574 | 114 | Minimum Margin | 4460 | 97.51% | above 1000 MW
20250606 | 2030 | June |  | 6093 | 523 | 4574 | 2 | Minimum Margin | 4572 | 99.96% | above 1000 MW
20250608 | 1830 | June |  | 7110 | 668 | 877 | 129 | Minimum Margin | 748 | 85.29% | [500-1000] MW
20250608 | 1930 | June |  | 6981 | 656 | 877 | 0 | Critical Branch | 877 | 100% | [500-1000] MW
20250608 | 2030 | June |  | 6981 | 656 | 877 | 0 | Critical Branch | 877 | 100% | [500-1000] MW
20250610 | 930 | June | 5487 |  |  | 469 | 262 | Minimum Margin | 207 | 44.14% | below 500 MW
20250610 | 1030 | June | 5458 |  |  | 469 | 233 | Minimum Margin | 236 | 50.32% | below 500 MW
20250610 | 1230 | June | 6609 |  |  | 818 | 596 | Minimum Margin | 222 | 27.14% | [500-1000] MW
20250610 | 1330 | June | 6609 |  |  | 818 | 596 | Minimum Margin | 222 | 27.14% | [500-1000] MW
20250610 | 1430 | June | 6609 |  |  | 818 | 596 | Minimum Margin | 222 | 27.14% | [500-1000] MW
20250610 | 1530 | June | 7041 |  |  | 2759 | 102 | Minimum Margin | 2657 | 96.3% | above 1000 MW
20250610 | 1630 | June | 7109 |  |  | 2759 | 170 | Minimum Margin | 2589 | 93.84% | above 1000 MW
20250610 | 1730 | June | 7103 |  |  | 2759 | 164 | Minimum Margin | 2595 | 94.06% | above 1000 MW
20250611 | 930 | June | 5713 |  |  | 4243 | 89 | Minimum Margin | 4154 | 97.9% | above 1000 MW
20250611 | 1030 | June | 5624 |  |  | 4243 | 0 | Critical Branch | 4243 | 100% | above 1000 MW
20250611 | 1130 | June | 5624 |  |  | 4243 | 0 | Critical Branch | 4243 | 100% | above 1000 MW
20250611 | 2130 | June |  | 7766 | 783 | 471 | 107 | Minimum Margin | 364 | 77.28% | below 500 MW
20250611 | 2230 | June |  | 7665 | 774 | 471 | 6 | Minimum Margin | 465 | 98.73% | below 500 MW
20250611 | 2330 | June |  | 7394 | 809 | 882 | 114 | Minimum Margin | 768 | 87.07% | [500-1000] MW
20250612 | 1830 | June |  | 6421 | 630 | 2590 | 168 | Minimum Margin | 2422 | 93.51% | above 1000 MW
20250612 | 1930 | June |  | 6338 | 621 | 2590 | 85 | Minimum Margin | 2505 | 96.72% | above 1000 MW
20250612 | 2030 | June |  | 6338 | 621 | 2590 | 85 | Minimum Margin | 2505 | 96.72% | above 1000 MW
20250613 | 930 | June | 6490 |  |  | 4521 | 25 | Minimum Margin | 4496 | 99.45% | above 1000 MW
20250613 | 1030 | June | 6536 |  |  | 4521 | 71 | Minimum Margin | 4450 | 98.43% | above 1000 MW
20250613 | 1130 | June | 6534 |  |  | 4521 | 69 | Minimum Margin | 4452 | 98.47% | above 1000 MW
20250616 | 930 | June | 6890 |  |  | 2751 | 160 | Minimum Margin | 2591 | 94.18% | above 1000 MW
20250616 | 1030 | June | 6890 |  |  | 2751 | 160 | Minimum Margin | 2591 | 94.18% | above 1000 MW
20250616 | 1130 | June | 6890 |  |  | 2751 | 160 | Minimum Margin | 2591 | 94.18% | above 1000 MW
20250616 | 1230 | June | 7379 |  |  | 4155 | 160 | Minimum Margin | 3995 | 96.15% | above 1000 MW
20250616 | 1330 | June | 7379 |  |  | 4155 | 160 | Minimum Margin | 3995 | 96.15% | above 1000 MW
20250616 | 1430 | June | 7379 |  |  | 4155 | 160 | Minimum Margin | 3995 | 96.15% | above 1000 MW
20250616 | 1530 | June | 6935 |  |  | 2737 | 153 | Minimum Margin | 2584 | 94.41% | above 1000 MW
20250616 | 1630 | June | 6935 |  |  | 2737 | 153 | Minimum Margin | 2584 | 94.41% | above 1000 MW
20250616 | 1730 | June | 6935 |  |  | 2737 | 153 | Minimum Margin | 2584 | 94.41% | above 1000 MW
20250618 | 730 | June | 7995 |  |  | 3153 | 0 | Critical Branch | 3153 | 100% | above 1000 MW
20250618 | 830 | June | 7996 |  |  | 3153 | 1 | Minimum Margin | 3152 | 99.97% | above 1000 MW
20250618 | 1230 | June | 7425 |  |  | 8255 | 329 | Minimum Margin | 7926 | 96.01% | above 1000 MW
20250618 | 1330 | June | 7425 |  |  | 8255 | 329 | Minimum Margin | 7926 | 96.01% | above 1000 MW
20250618 | 1430 | June | 7425 |  |  | 8255 | 329 | Minimum Margin | 7926 | 96.01% | above 1000 MW
20250618 | 1830 | June |  | 6566 | 503 | 4051 | 116 | Minimum Margin | 3935 | 97.14% | above 1000 MW
20250618 | 1930 | June |  | 6458 | 495 | 4051 | 8 | Minimum Margin | 4043 | 99.8% | above 1000 MW
20250618 | 2030 | June |  | 6480 | 496 | 4051 | 30 | Minimum Margin | 4021 | 99.26% | above 1000 MW
20250619 | 730 | June | 8074 |  |  | 3301 | 157 | Minimum Margin | 3144 | 95.24% | above 1000 MW
20250619 | 830 | June | 8053 |  |  | 3301 | 136 | Minimum Margin | 3165 | 95.88% | above 1000 MW
20250619 | 1830 | June |  | 8546 | 661 | 1195 | 155 | Minimum Margin | 1040 | 87.03% | above 1000 MW
20250619 | 1930 | June |  | 8856 | 685 | 1195 | 465 | Minimum Margin | 730 | 61.09% | above 1000 MW
20250619 | 2030 | June |  | 8856 | 685 | 1195 | 465 | Minimum Margin | 730 | 61.09% | above 1000 MW
20250621 | 1830 | June |  | 8414 | 651 | 2048 | 461 | Minimum Margin | 1587 | 77.49% | above 1000 MW
20250621 | 1930 | June |  | 8414 | 651 | 2048 | 461 | Minimum Margin | 1587 | 77.49% | above 1000 MW
20250621 | 2030 | June |  | 8414 | 651 | 2048 | 461 | Minimum Margin | 1587 | 77.49% | above 1000 MW
20250622 | 330 | June | 8687 |  |  | 1145 | 573 | Minimum Margin | 572 | 49.96% | above 1000 MW
20250622 | 430 | June | 8489 |  |  | 1145 | 375 | Minimum Margin | 770 | 67.25% | above 1000 MW
20250622 | 530 | June | 8687 |  |  | 1145 | 573 | Minimum Margin | 572 | 49.96% | above 1000 MW
20250622 | 630 | June | 8529 |  |  | 1145 | 415 | Minimum Margin | 730 | 63.76% | above 1000 MW
20250622 | 1230 | June | 7151 |  |  | 596 | 463 | Minimum Margin | 133 | 22.32% | [500-1000] MW
20250622 | 1330 | June | 6967 |  |  | 596 | 279 | Minimum Margin | 317 | 53.19% | [500-1000] MW
20250622 | 1430 | June | 7226 |  |  | 596 | 538 | Minimum Margin | 58 | 9.732% | [500-1000] MW
20250623 | 1330 | June | 6617 |  |  | 227 | 119 | Minimum Margin | 108 | 47.58% | below 500 MW
20250624 | 930 | June | 5881 |  |  | 421 | 0 | Critical Branch | 421 | 100% | below 500 MW
20250624 | 1030 | June | 6123 |  |  | 421 | 242 | Minimum Margin | 179 | 42.52% | below 500 MW
20250624 | 1130 | June | 5963 |  |  | 421 | 82 | Minimum Margin | 339 | 80.52% | below 500 MW
20250624 | 1230 | June | 5635 |  |  | 693 | 186 | Minimum Margin | 507 | 73.16% | [500-1000] MW
20250624 | 1330 | June | 5449 |  |  | 693 | 0 | Critical Branch | 693 | 100% | [500-1000] MW
20250624 | 1430 | June | 5681 |  |  | 693 | 232 | Minimum Margin | 461 | 66.52% | [500-1000] MW
20250624 | 1530 | June | 5451 |  |  | 785 | 155 | Minimum Margin | 630 | 80.25% | [500-1000] MW
20250625 | 930 | June | 7128 |  |  | 211 | 0 | Critical Branch | 211 | 100% | below 500 MW
20250625 | 1130 | June | 7129 |  |  | 211 | 1 | Minimum Margin | 210 | 99.53% | below 500 MW

## DA TTC Validation
DA Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | ANTC |  |  | LimitedBy |  | TTC Validation Reduction |  |  | Reason for TTC Reduction
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | Smoothing | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason
20250401 | April | 30 | 7815 |  |  | 7815 |  |  | -4387 | -4387 | -4386 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 395
20250401 | April | 130 | 7815 |  |  | 7815 |  |  | -4387 | -4387 | -4386 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 366
20250401 | April | 230 | 7815 |  |  | 7815 |  |  | -4387 | -4387 | -4386 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 366
20250401 | April | 330 | 7282 |  |  | 7282 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 366
20250401 | April | 430 | 7282 |  |  | 7282 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 364
20250401 | April | 530 | 7282 |  |  | 7282 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 205 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 630 | 7082 |  |  | 7081 |  |  | -3251 | -3251 | -3250 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 208 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 730 |  | 8191 | 1067 |  | 7868 | 1032 | 3379 | 185 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -337 | NA | -5804 |  |  | AT | 349
20250401 | April | 830 |  | 8191 | 1067 |  | 7868 | 1032 | 3379 | 185 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -237 | NA | -5804 |  |  | AT | 349
20250401 | April | 930 | 7225 |  |  | 7215 |  |  | 3929 | 235 | 3704 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 349
20250401 | April | 1030 | 7225 |  |  | 7215 |  |  | 3929 | 235 | 3704 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 424
20250401 | April | 1130 | 7225 |  |  | 7215 |  |  | 3929 | 235 | 3704 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 424
20250401 | April | 1230 | 8674 |  |  | 8633 |  |  | -1422 | -1422 | -1381 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 424
20250401 | April | 1330 | 8674 |  |  | 8633 |  |  | -1422 | -1422 | -1381 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 424
20250401 | April | 1430 | 8674 |  |  | 8633 |  |  | -1422 | -1422 | -1381 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 424
20250401 | April | 1530 | 8666 |  |  | 8666 |  |  | -1143 | -1143 | -1143 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 424
20250401 | April | 1630 | 8666 |  |  | 8666 |  |  | -1143 | -1143 | -1143 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 1730 | 8666 |  |  | 8666 |  |  | -1143 | -1143 | -1143 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 1830 |  | 9059 | 899 |  | 8640 | 899 | -6540 | -6540 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 931 | NA | -6842 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250401 | April | 1930 |  | 9059 | 899 |  | 8640 | 899 | -6540 | -6540 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1031 | NA | -6842 |  |  | AT | 399
20250401 | April | 2030 |  | 9059 | 899 |  | 8640 | 899 | -6540 | -6540 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1131 | NA | -6842 |  |  | AT | 399
20250401 | April | 2130 | 8367 |  |  | 8366 |  |  | -4888 | -4888 | -4888 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 381
20250401 | April | 2230 | 8367 |  |  | 8366 |  |  | -4888 | -4888 | -4888 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250401 | April | 2330 | 7557 |  |  | 7557 |  |  | -4078 | -4078 | -4077 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250402 | April | 30 | 7637 |  |  | 7636 |  |  | -3279 | -3279 | -3278 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250402 | April | 130 | 7637 |  |  | 7636 |  |  | -3279 | -3279 | -3278 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 355
20250402 | April | 230 | 7637 |  |  | 7636 |  |  | -3279 | -3279 | -3278 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 355
20250402 | April | 330 | 7078 |  |  | 7078 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 355
20250402 | April | 430 | 7078 |  |  | 7078 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 353
20250402 | April | 530 | 7078 |  |  | 7078 |  |  | -2114 | -2114 | -2113 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 409
20250402 | April | 630 | 6878 |  |  | 6878 |  |  | -1908 | -1908 | -1907 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 417
20250402 | April | 730 | 8541 |  |  | 8378 |  |  | -5293 | -5293 | -5133 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 350
20250402 | April | 830 | 8541 |  |  | 8540 |  |  | -5293 | -5293 | -5293 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 350
20250402 | April | 930 | 7250 |  |  | 7245 |  |  | 972 | 260 | 716 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 350
20250402 | April | 1030 | 7244 |  |  | 7240 |  |  | 972 | 254 | 722 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415
20250402 | April | 1130 | 7243 |  |  | 7239 |  |  | 972 | 253 | 723 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415
20250402 | April | 1230 | 8495 |  |  | 8495 |  |  | 1412 | 273 | 1139 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250402 | April | 1330 | 8495 |  |  | 8495 |  |  | 1412 | 273 | 1139 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 438
20250402 | April | 1430 | 8495 |  |  | 8495 |  |  | 1412 | 273 | 1139 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 438
20250402 | April | 1530 | 8946 |  |  | 8945 |  |  | -1634 | -1634 | -1633 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 438
20250402 | April | 1630 | 8946 |  |  | 8945 |  |  | -1634 | -1634 | -1633 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 1730 | 8946 |  |  | 8945 |  |  | -1634 | -1634 | -1633 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 1830 |  | 8618 | 832 |  | 8408 | 832 | -1810 | -1810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 998 | NA | -6744 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 1930 |  | 8618 | 832 |  | 8408 | 832 | -1810 | -1810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1098 | NA | -6744 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 2030 |  | 8618 | 832 |  | 8408 | 832 | -1810 | -1810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1198 | NA | -6744 |  |  | AT | 450 | Reduction because NTC over thermal limit on border |  |  |  |  | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 2130 | 9592 |  |  | 9307 |  |  | -2312 | -2312 | -2071 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3230 | Planned outage of Creys-Saint-Vulbas 2
20250402 | April | 2230 | 9592 |  |  | 9307 |  |  | -2312 | -2312 | -2071 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 386
20250402 | April | 2330 | 8782 |  |  | 8668 |  |  | -1464 | -1464 | -1368 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 386
20250403 | April | 30 | 7652 |  |  | 7652 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 386
20250403 | April | 130 | 7652 |  |  | 7652 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 359
20250403 | April | 230 | 7652 |  |  | 7652 |  |  | -3454 | -3454 | -3454 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 359
20250403 | April | 330 | 7153 |  |  | 7152 |  |  | -2501 | -2501 | -2500 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 359
20250403 | April | 430 | 7153 |  |  | 7152 |  |  | -2501 | -2501 | -2500 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250403 | April | 530 | 7153 |  |  | 7152 |  |  | -2501 | -2501 | -2500 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250403 | April | 630 | 6953 |  |  | 6952 |  |  | -2298 | -2298 | -2297 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250403 | April | 730 | 8542 |  |  | 8452 |  |  | -4394 | -4394 | -4294 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 400
20250403 | April | 830 | 8542 |  |  | 8500 |  |  | -4394 | -4394 | -4342 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 400
20250403 | April | 930 | 7046 |  |  | 7046 |  |  | -2722 | -2722 | -2721 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 400
20250403 | April | 1030 | 7046 |  |  | 7046 |  |  | -2722 | -2722 | -2721 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250403 | April | 1130 | 7046 |  |  | 7046 |  |  | -2722 | -2722 | -2721 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250403 | April | 1230 | 8136 |  |  | 8119 |  |  | -4732 | -4732 | -4721 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250403 | April | 1330 | 8136 |  |  | 8119 |  |  | -4732 | -4732 | -4721 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 370
20250403 | April | 1430 | 8136 |  |  | 8057 |  |  | -4732 | -4732 | -4658 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 370
20250403 | April | 1530 | 6557 |  |  | 6557 |  |  | -2978 | -2978 | -2977 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 382
20250403 | April | 1630 | 6557 |  |  | 6557 |  |  | -2978 | -2978 | -2977 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 339
20250403 | April | 1730 | 7857 |  |  | 7857 |  |  | -4237 | -4237 | -4237 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 339
20250403 | April | 1830 |  | 6579 | 392 |  | 6578 | 392 | -1854 | -1854 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 1438 | NA | -5794 |  |  | AT | 339
20250403 | April | 1930 |  | 6579 | 392 |  | 6578 | 392 | -1854 | -1854 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 1538 | NA | -5794 |  |  | AT | 339
20250403 | April | 2030 |  | 6579 | 392 |  | 6578 | 392 | -1854 | -1854 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 1638 | NA | -5794 |  |  | AT | 339
20250403 | April | 2130 | 7190 |  |  | 7189 |  |  | -2895 | -2895 | -2895 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 317
20250404 | April | 30 | 7025 |  |  | 7006 |  |  | 1910 | 196 | 1733 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6756 | Reduction due to missing redispatch potential
20250404 | April | 130 | 7025 |  |  | 7006 |  |  | 1910 | 196 | 1733 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6756 | Reduction due to missing redispatch potential
20250404 | April | 230 | 7025 |  |  | 7006 |  |  | 1910 | 196 | 1733 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6756 | Reduction due to missing redispatch potential
20250404 | April | 330 | 6699 |  |  | 6687 |  |  | 3428 | 219 | 3221 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6437 | Reduction due to missing redispatch potential
20250404 | April | 430 | 6699 |  |  | 6687 |  |  | 3428 | 219 | 3221 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6437 | Reduction due to missing redispatch potential
20250404 | April | 530 | 6699 |  |  | 6687 |  |  | 3428 | 219 | 3221 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6437 | Reduction due to missing redispatch potential | FR | 2536 | Process fail during TSO validation phase
20250404 | April | 630 | 6493 |  |  | 6482 |  |  | 3394 | 213 | 3192 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6232 | Reduction due to missing redispatch potential | FR | 2536 | Process fail during TSO validation phase
20250404 | April | 1830 | 7771 |  |  | 7752 |  |  | 5953 | 181 | 5791 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7502 | Reduction due to missing redispatch potential
20250404 | April | 1930 | 7771 |  |  | 7752 |  |  | 5953 | 181 | 5791 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7502 | Reduction due to missing redispatch potential
20250404 | April | 2030 | 7771 |  |  | 7752 |  |  | 5953 | 181 | 5791 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7502 | Reduction due to missing redispatch potential
20250404 | April | 2130 | 7776 |  |  | 7758 |  |  | 4813 | 186 | 4645 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7508 | Reduction due to missing redispatch potential
20250404 | April | 2230 | 7776 |  |  | 7758 |  |  | 4813 | 186 | 4645 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7508 | Reduction due to missing redispatch potential
20250404 | April | 2330 | 6956 |  |  | 6940 |  |  | 5025 | 176 | 4865 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6690 | Reduction due to missing redispatch potential
20250405 | April | 630 | 7113 |  |  | 6250 |  |  | 390 | 233 | 1020 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250405 | April | 730 | 7801 |  |  | 5480 |  |  | 677 | 211 | 2787 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6391 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | IT | 5230 | Foreseen violations on the border
20250405 | April | 830 | 7796 |  |  | 5480 |  |  | 677 | 206 | 2787 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6388 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | IT | 5230 | Foreseen violations on the border
20250405 | April | 930 | 8293 |  |  | 6980 |  |  | -4706 | -4706 | -3393 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250405 | April | 1330 | 7986 |  |  | 7986 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | NA | NA | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 1430 | 7986 |  |  | 7986 |  |  | -2061 | -2061 | -2061 | Critical Branch | Critical Branch | NA | NA | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 1530 | 9397 |  |  | 8960 |  |  | -1577 | -1577 | -1208 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 2230 | 7767 |  |  | 7747 |  |  | 666 | 177 | 509 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250405 | April | 2330 | 6947 |  |  | 6929 |  |  | 1080 | 167 | 931 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 30 | 9209 |  |  | 8646 |  |  | -4347 | -4347 | -3603 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 130 | 9209 |  |  | 8646 |  |  | -4347 | -4347 | -3603 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 230 | 9209 |  |  | 8646 |  |  | -4347 | -4347 | -3603 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 330 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 430 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 530 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 402
20250406 | April | 630 | 8685 |  |  | 8361 |  |  | -5804 | -5804 | -5489 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 402
20250406 | April | 730 | 8323 |  |  | 8322 |  |  | -5552 | -5552 | -5551 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 424 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 830 | 8323 |  |  | 8322 |  |  | -5552 | -5552 | -5551 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 424 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 930 | 8743 |  |  | 8394 |  |  | -1336 | -1336 | -1037 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 424 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1030 | 8743 |  |  | 8394 |  |  | -1336 | -1336 | -1037 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 407
20250406 | April | 1130 | 8743 |  |  | 8394 |  |  | -1336 | -1336 | -1037 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 407
20250406 | April | 1230 | 8421 |  |  | 8420 |  |  | -1423 | -1423 | -1423 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 400
20250406 | April | 1330 | 8421 |  |  | 8420 |  |  | -1423 | -1423 | -1423 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 323
20250406 | April | 1430 | 8421 |  |  | 7750 |  |  | -1423 | -1423 | -753 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 323
20250406 | April | 1530 |  | 6266 | 418 |  | 5974 | 418 | -4347 | -4347 | 0 | TTC Selection - LTTCImport and LTTCExport | Validation phase | 1112 | NA | -5138 |  |  | AT | 323
20250406 | April | 1630 |  | 6266 | 418 |  | 5974 | 418 | -4347 | -4347 | 0 | TTC Selection - LTTCImport and LTTCExport | Validation phase | 1212 | NA | -5138 |  |  | AT | 400 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1730 |  | 6266 | 418 |  | 5974 | 418 | -4347 | -4347 | 0 | TTC Selection - LTTCImport and LTTCExport | Validation phase | 1312 | NA | -5138 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1830 | 9008 |  |  | 7750 |  |  | -5645 | -5645 | -4393 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 1930 | 9008 |  |  | 8542 |  |  | -5645 | -5645 | -5196 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 2030 | 9008 |  |  | 8542 |  |  | -5645 | -5645 | -5196 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 2130 | 8688 |  |  | 8362 |  |  | -5634 | -5634 | -5320 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250406 | April | 2230 | 8688 |  |  | 8362 |  |  | -5634 | -5634 | -5320 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250406 | April | 2330 | 8688 |  |  | 8362 |  |  | -5634 | -5634 | -5320 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250407 | April | 30 |  | 7812 | 734 |  | 7803 | 734 | -865 | -865 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -704 | NA | -6335 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250407 | April | 130 |  | 7812 | 734 |  | 7803 | 734 | -865 | -865 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -604 | NA | -6335 |  |  | AT | 424 |  |  |  |  | FR | 2975 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 230 |  | 7812 | 734 |  | 7803 | 734 | -865 | -865 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -504 | NA | -6335 |  |  | AT | 424 |  |  |  |  | FR | 2975 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 330 |  | 7501 | 734 |  | 7493 | 734 | 335 | 179 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -404 | NA | -6025 |  |  | AT | 424 |  |  |  |  | FR | 2975 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 430 |  | 7501 | 734 |  | 7493 | 734 | 335 | 179 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -304 | NA | -6025 |  |  | AT | 425 |  |  |  |  | FR | 2975 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 530 |  | 7501 | 734 |  | 7493 | 734 | 335 | 179 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -204 | NA | -6025 |  |  | AT | 432 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 630 |  | 7335 | 737 |  | 7322 | 737 | 343 | 213 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -107 | NA | -5848 |  |  | AT | 432 |  |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 730 |  | 8098 | 732 |  | 7999 | 732 | -4363 | -4363 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -2 | NA | -6535 |  |  | AT | 337 |  |  |  |  | FR | 2480 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 830 |  | 8098 | 732 |  | 7999 | 732 | -4363 | -4363 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 98 | NA | -6535 |  |  | AT | 337 |  |  |  |  | FR | 2480 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 930 | 7040 |  |  | 6940 |  |  | -3573 | -3573 | -3480 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 337 |  |  |  |  | FR | 2480 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1030 | 7040 |  |  | 6940 |  |  | -3573 | -3573 | -3480 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 384 |  |  |  |  | FR | 2837 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1130 | 7040 |  |  | 6940 |  |  | -3573 | -3573 | -3480 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 384 |  |  |  |  | FR | 2837 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1230 | 7946 |  |  | 6117 |  |  | -1266 | -1266 | 563 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 384 |  |  |  |  | FR | 2837 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1330 | 7946 |  |  | 6117 |  |  | -1266 | -1266 | 563 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 348 |  |  |  |  | FR | 2563 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1430 | 7946 |  |  | 6117 |  |  | -1266 | -1266 | 563 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 348 |  |  |  |  | FR | 2563 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1530 | 7250 |  |  | 7150 |  |  | -3448 | -3448 | -3356 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 348 |  |  |  |  | FR | 2563 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1630 | 7250 |  |  | 7150 |  |  | -3448 | -3448 | -3356 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 208 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1730 | 7250 |  |  | 7150 |  |  | -3448 | -3448 | -3356 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 215 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1830 |  | 8394 | 947 |  | 8016 | 935 | -4370 | -4370 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 883 | NA | -6146 |  |  | AT | 215 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 1930 |  | 8394 | 947 |  | 8046 | 935 | -4370 | -4370 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 983 | NA | -6176 |  |  | AT | 402
20250407 | April | 2030 |  | 8394 | 947 |  | 8046 | 935 | -4370 | -4370 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1083 | NA | -6176 |  |  | AT | 402
20250407 | April | 2130 |  | 7752 | 831 |  | 7752 | 831 | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1299 | NA | -6090 |  |  | AT | 381
20250407 | April | 2230 |  | 7752 | 831 |  | 7752 | 831 | -997 | -997 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1399 | NA | -6090 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250407 | April | 2330 |  | 6997 | 851 |  | 6997 | 851 | -106 | -106 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1479 | NA | -5295 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250408 | April | 30 |  | 9039 | 913 |  | 8392 | 913 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -883 | NA | -6566 |  |  | AT | 435 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
20250408 | April | 130 |  | 9039 | 913 |  | 8392 | 913 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -783 | NA | -6566 |  |  | AT | 390
20250408 | April | 230 |  | 9039 | 913 |  | 8392 | 913 | -3169 | -3169 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -683 | NA | -6566 |  |  | AT | 390
20250408 | April | 330 |  | 7163 | 665 |  | 7162 | 665 | 2086 | 222 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -335 | NA | -5832 |  |  | AT | 390
20250408 | April | 430 |  | 7163 | 665 |  | 7162 | 665 | 2086 | 222 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -235 | NA | -5832 |  |  | AT | 377
20250408 | April | 530 |  | 7163 | 665 |  | 7162 | 665 | 2086 | 222 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -135 | NA | -5832 |  |  | AT | 187
20250408 | April | 630 |  | 6767 | 647 |  | 6766 | 647 | 2112 | 25 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -17 | NA | -5472 |  |  | AT | 187
20250408 | April | 730 |  | 7175 | 787 |  | 7175 | 786 | -4319 | -4319 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -57 | NA | -5603 |  |  | AT | 450
20250408 | April | 830 |  | 7175 | 787 |  | 7175 | 786 | -4319 | -4319 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 43 | NA | -5603 |  |  | AT | 450
20250408 | April | 930 | 9210 |  |  | 9210 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 428
20250408 | April | 1030 | 9210 |  |  | 9210 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 351
20250408 | April | 1130 | 9210 |  |  | 8796 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 351
20250408 | April | 1230 | 7296 |  |  | 7296 |  |  | 8747 | 256 | 8491 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 351
20250408 | April | 1330 | 7296 |  |  | 7296 |  |  | 8747 | 256 | 8491 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 428
20250408 | April | 1430 | 7295 |  |  | 7295 |  |  | 8747 | 255 | 8492 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450
20250408 | April | 1530 | 9210 |  |  | 7976 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450
20250408 | April | 1630 | 9210 |  |  | 7976 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 196
20250408 | April | 1730 | 9210 |  |  | 7976 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 196
20250408 | April | 1830 |  | 7506 | 793 |  | 7506 | 793 | 6744 | 174 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1037 | NA | -5920 |  |  | AT | 196
20250408 | April | 1930 |  | 7441 | 787 |  | 7441 | 786 | 6744 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1143 | NA | -5869 |  |  | AT | 429
20250408 | April | 2030 |  | 7523 | 795 |  | 7523 | 795 | 6744 | 191 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1235 | NA | -5933 |  |  | AT | 429
20250408 | April | 2130 |  | 8245 | 680 |  | 8244 | 680 | -2758 | -2758 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1450 | NA | -6884 |  |  | AT | 410
20250408 | April | 2230 |  | 8245 | 680 |  | 8244 | 680 | -2758 | -2758 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1550 | NA | -6884 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250408 | April | 2330 |  | 7492 | 700 |  | 7492 | 700 | -1906 | -1906 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1630 | NA | -6092 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 30 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1030 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1130 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1230 | 9210 |  |  | 7450 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2 | SI | 7433 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250409 | April | 1330 | 9210 |  |  | 7450 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2 | SI | 7433 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250409 | April | 1430 | 9210 |  |  | 7450 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2 | SI | 7433 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250409 | April | 1530 | 9210 |  |  | 8375 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1630 | 9210 |  |  | 8375 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1730 | 9210 |  |  | 8375 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1830 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 1930 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2030 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2130 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2230 | 9410 |  |  | 8575 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250409 | April | 2330 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 30 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 130 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 230 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 330 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 430 | 8600 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 730 |  | 6434 | 395 |  | 5926 | 395 | 6894 | 2 | 0 | Minimum Margin | Validation phase | 335 | NA | -5136 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250410 | April | 830 |  | 6649 | 413 |  | 6142 | 413 | 6894 | 218 | 0 | Minimum Margin | Validation phase | 417 | NA | -5316 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250410 | April | 1030 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1130 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1230 | 8254 |  |  | 7787 |  |  | 5989 | 214 | 6878 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1630 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1730 | 7040 |  |  | 7040 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 1830 | 9410 |  |  | 8540 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250410 | April | 2230 | 7489 |  |  | 7482 |  |  | 5684 | 249 | 5442 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 338
20250410 | April | 2330 | 6664 |  |  | 6658 |  |  | 5905 | 234 | 5677 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 338
20250411 | April | 30 | 7080 |  |  | 7059 |  |  | 2688 | 200 | 2509 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 337
20250411 | April | 130 | 7069 |  |  | 7049 |  |  | 2688 | 189 | 2519 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 414 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 230 | 7047 |  |  | 7030 |  |  | 2688 | 167 | 2538 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 435 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 330 | 8950 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 430 | 8950 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 435 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 530 | 8950 |  |  | 7912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 630 | 8750 |  |  | 7712 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 730 | 9560 |  |  | 7003 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 830 | 9560 |  |  | 7003 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 930 | 9560 |  |  | 7555 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 |  |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1030 | 9560 |  |  | 7555 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | -155 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1130 | 9560 |  |  | 7555 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 62 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1230 | 8123 |  |  | 7531 |  |  | 4398 | 204 | 5526 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 377 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
20250411 | April | 1330 | 8123 |  |  | 7531 |  |  | 4398 | 204 | 5526 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 260 | Reduction because NTC over thermal limit on border
20250411 | April | 1430 | 8123 |  |  | 7531 |  |  | 4398 | 204 | 5526 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 342 | Reduction because NTC over thermal limit on border
20250411 | April | 1530 | 7390 |  |  | 7390 |  |  | -3804 | -3804 | -3804 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 |  |  | AT | 347 | Reduction because NTC over thermal limit on border
20250411 | April | 1630 | 7390 |  |  | 7390 |  |  | -3804 | -3804 | -3804 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 |  |  | AT | 355 | Reduction because NTC over thermal limit on border
20250411 | April | 1730 | 7890 |  |  | 7890 |  |  | -4290 | -4290 | -4290 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 |  |  | AT | 357 | Reduction because NTC over thermal limit on border
20250411 | April | 1830 |  | 7573 | 489 |  | 7573 | 489 | 3464 | 107 | 0 | Minimum Margin | Minimum Margin | 1341 | NA | -6595 |  |  | AT | 360 | Reduction because NTC over thermal limit on border
20250411 | April | 1930 |  | 7610 | 492 |  | 7610 | 492 | 3464 | 144 | 0 | Minimum Margin | Minimum Margin | 1438 | NA | -6626 |  |  | AT | 356 | Reduction because NTC over thermal limit on border
20250411 | April | 2030 |  | 7672 | 496 |  | 7672 | 496 | 3464 | 207 | 0 | Minimum Margin | Minimum Margin | 1534 | NA | -6680 |  |  | AT | 299 | Reduction because NTC over thermal limit on border
20250411 | April | 2130 | 8252 |  |  | 8235 |  |  | 3499 | 162 | 3354 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 338
20250412 | April | 730 | 8090 |  |  | 7603 |  |  | -4067 | -4067 | -3580 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 7353 | Foreseen violations on the border
20250412 | April | 830 | 8090 |  |  | 7603 |  |  | -4067 | -4067 | -3580 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 7353 | Foreseen violations on the border
20250412 | April | 930 | 9277 |  |  | 9103 |  |  | -3733 | -3733 | -3559 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250412 | April | 1530 | 10260 |  |  | 9397 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 9147 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250412 | April | 1630 | 10260 |  |  | 9397 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 9147 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250412 | April | 1730 | 10260 |  |  | 8197 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 9147 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | IT | 7947 | Foreseen violations on the border
20250413 | April | 930 | 8975 |  |  | 7517 |  |  | -1276 | -1276 | 182 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7267 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1030 | 8975 |  |  | 7517 |  |  | -1276 | -1276 | 182 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7267 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1130 | 8975 |  |  | 7517 |  |  | -1276 | -1276 | 182 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7267 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1230 | 8486 |  |  | 7479 |  |  | -440 | -440 | 567 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7229 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1330 | 8486 |  |  | 7479 |  |  | -440 | -440 | 567 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7229 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1430 | 8486 |  |  | 7479 |  |  | -440 | -440 | 567 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7229 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250413 | April | 1530 | 9289 |  |  | 8015 |  |  | -1601 | -1601 | -327 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7765 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20250413 | April | 1630 | 9589 |  |  | 8315 |  |  | -1944 | -1944 | -670 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 8065 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 3463 | Process fail during TSO validation phase
20250413 | April | 1730 | 9589 |  |  | 8315 |  |  | -1944 | -1944 | -670 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 8065 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 3463 | Process fail during TSO validation phase
20250413 | April | 1830 |  | 7840 | 618 |  | 7758 | 618 | 2818 | 169 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1212 | NA | -6522 | [8 empty] | FR | 3463 | Process fail during TSO validation phase
20250413 | April | 2130 | 8403 |  |  | 8397 |  |  | 4720 | 56 | 4670 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 8147 | Reduction due to missing redispatch potential
20250413 | April | 2230 | 8525 |  |  | 8505 |  |  | 4720 | 178 | 4562 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 8255 | Reduction due to missing redispatch potential
20250413 | April | 2330 | 8499 |  |  | 8482 |  |  | 4720 | 152 | 4585 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 8232 | Reduction due to missing redispatch potential
20250414 | April | 530 |  | 7833 | 625 |  | 7833 | 625 | -3353 | -3353 | 0 | Critical Branch | Min import NTC Threshold | -95 | NA | -6583 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 630 |  | 7633 | 625 |  | 7216 | 625 | -3182 | -3182 | 0 | Critical Branch | Smoothing ramp | 5 | NA | -5966 | Smoothing | Smoothing ramp | [6 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 730 | 7490 |  |  | 6000 |  |  | -1255 | -1255 | 593 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250414 | April | 830 | 7290 |  |  | 5949 |  |  | -1180 | -1180 | 574 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250414 | April | 930 | 7290 |  |  | 6573 |  |  | -838 | -838 | 864 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1030 | 7290 |  |  | 6573 |  |  | -838 | -838 | 864 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1130 | 7290 |  |  | 6573 |  |  | -838 | -838 | 864 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1230 | 7376 |  |  | 5736 |  |  | -2705 | -2705 | -1077 | Critical Branch | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1330 | 7376 |  |  | 5736 |  |  | -2705 | -2705 | -1077 | Critical Branch | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1430 | 7376 |  |  | 5736 |  |  | -2705 | -2705 | -1077 | Critical Branch | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1530 | 7371 |  |  | 6622 |  |  | -2642 | -2642 | -869 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1630 | 7371 |  |  | 6622 |  |  | -2642 | -2642 | -869 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1730 | 7371 |  |  | 6622 |  |  | -2642 | -2642 | -869 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1830 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 1930 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2030 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2130 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2230 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250414 | April | 2330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 30 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 130 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 230 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 430 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 530 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 630 | 8650 |  |  | 7212 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 730 | 9460 |  |  | 6434 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6808 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 830 | 9460 |  |  | 6434 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6808 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 930 | 9460 |  |  | 6708 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7264 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1030 | 9460 |  |  | 6708 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7264 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1130 | 9460 |  |  | 6708 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7264 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1230 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8168 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1330 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8168 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1430 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8168 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1530 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8166 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1630 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8166 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1730 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8166 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250415 | April | 1830 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 1930 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2030 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2130 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2230 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250415 | April | 2330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 30 | 7045 |  |  | 6345 |  |  | 2149 | 222 | 3535 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 130 | 7045 |  |  | 6345 |  |  | 2149 | 222 | 3535 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 230 | 7045 |  |  | 6345 |  |  | 2149 | 222 | 3535 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 330 | 7003 |  |  | 6320 |  |  | 2989 | 223 | 4331 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 430 | 7003 |  |  | 6320 |  |  | 2989 | 223 | 4331 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 530 | 7003 |  |  | 6320 |  |  | 2989 | 223 | 4331 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 630 | 6648 |  |  | 6053 |  |  | 2967 | 68 | 4237 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 730 | 7315 |  |  | 6588 |  |  | 3420 | 25 | 5119 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 830 | 7542 |  |  | 6720 |  |  | 3420 | 252 | 5108 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 930 | 7542 |  |  | 6723 |  |  | 1972 | 252 | 3662 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1030 | 7545 |  |  | 6725 |  |  | 1972 | 255 | 3662 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1130 | 7543 |  |  | 6724 |  |  | 1972 | 253 | 3662 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1230 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8168 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1330 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8168 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1430 | 9460 |  |  | 7250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8168 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1530 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8166 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1630 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8166 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1730 | 9460 |  |  | 7249 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8166 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250416 | April | 1830 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 1930 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2030 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2130 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2230 | 9660 |  |  | 8075 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250416 | April | 2330 | 8850 |  |  | 7412 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 30 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 130 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 230 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 330 | 6780 |  |  | 6403 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 430 | 6780 |  |  | 6403 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 530 | 6780 |  |  | 6403 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 630 | 6580 |  |  | 6224 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 730 | 9460 |  |  | 7302 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7828 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 830 | 9460 |  |  | 7302 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7828 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 930 | 9460 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8035 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1030 | 9460 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8035 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1130 | 9460 |  |  | 7425 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8035 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1230 | 7290 |  |  | 6212 |  |  | -3141 | -3141 | -1896 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1330 | 7290 |  |  | 6212 |  |  | -3141 | -3141 | -1896 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1430 | 7290 |  |  | 6212 |  |  | -3141 | -3141 | -1896 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1530 | 9460 |  |  | 7478 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8123 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1630 | 9460 |  |  | 7478 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8123 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1730 | 9460 |  |  | 7478 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8123 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250417 | April | 1830 | 7515 |  |  | 6977 |  |  | 2792 | 25 | 4060 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 1930 | 7523 |  |  | 6982 |  |  | 2792 | 33 | 4059 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2030 | 7525 |  |  | 6983 |  |  | 2792 | 35 | 4059 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2130 | 7490 |  |  | 6962 |  |  | -924 | -924 | 349 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2230 | 7490 |  |  | 6962 |  |  | -924 | -924 | 349 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250417 | April | 2330 | 6680 |  |  | 6344 |  |  | -409 | -409 | 364 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 30 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 130 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 230 | 8850 |  |  | 7612 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 330 | 7006 |  |  | 6530 |  |  | 2400 | 226 | 3257 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 430 | 7006 |  |  | 6530 |  |  | 2400 | 226 | 3257 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 530 | 7006 |  |  | 6530 |  |  | 2400 | 226 | 3257 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2
20250418 | April | 630 | 7006 |  |  | 6140 |  |  | 2400 | 226 | 3287 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 730 | 7430 |  |  | 6335 |  |  | 4160 | 240 | 5015 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 830 | 7430 |  |  | 6335 |  |  | 4160 | 240 | 5015 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 930 | 9360 |  |  | 7624 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7985 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1030 | 9360 |  |  | 7568 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7895 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1130 | 9360 |  |  | 7568 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7895 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1230 | 9360 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1330 | 9360 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1430 | 9360 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1530 | 9660 |  |  | 7520 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2200 | Planned outage of Chaffard-Grande-Ile 2 | SI | 8223 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1630 | 9660 |  |  | 7520 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 8223 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250418 | April | 1730 | 10360 |  |  | 7181 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 8573 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 530 | 8950 |  |  | 8335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250419 | April | 630 | 8950 |  |  | 6835 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250419 | April | 730 | 9760 |  |  | 5335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250419 | April | 830 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 930 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1030 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1130 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1230 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1330 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1430 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1530 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1630 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1730 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1830 | 9760 |  |  | 3835 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250419 | April | 1930 | 9760 |  |  | 5335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250419 | April | 2030 | 9760 |  |  | 6835 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250419 | April | 2130 | 9760 |  |  | 8335 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250420 | April | 630 | 7754 |  |  | 6830 |  |  | -3097 | -3097 | -2170 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250420 | April | 730 | 9250 |  |  | 5330 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250420 | April | 830 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 930 | 7080 |  |  | 3830 |  |  | -3081 | -3081 | 169 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1030 | 7080 |  |  | 3830 |  |  | -3081 | -3081 | 169 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1130 | 7080 |  |  | 3830 |  |  | -3081 | -3081 | 169 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1230 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1330 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1430 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1530 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1630 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1730 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1830 | 7443 |  |  | 3830 |  |  | 3544 | 144 | 7013 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250420 | April | 1930 | 7443 |  |  | 5330 |  |  | 3544 | 144 | 5497 | Minimum Margin | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250420 | April | 2030 | 7443 |  |  | 6830 |  |  | 3544 | 144 | 4008 | Minimum Margin | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250421 | April | 630 | 8033 |  |  | 6830 |  |  | -3409 | -3409 | -2203 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250421 | April | 730 | 7233 |  |  | 5330 |  |  | -727 | -727 | 1193 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250421 | April | 830 | 7233 |  |  | 3830 |  |  | -727 | -727 | 2676 | Critical Branch | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 930 | 7080 |  |  | 3830 |  |  | -3519 | -3519 | -269 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1030 | 7080 |  |  | 3830 |  |  | -3519 | -3519 | -269 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1130 | 7080 |  |  | 3830 |  |  | -3519 | -3519 | -269 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1230 | 7080 |  |  | 3830 |  |  | -2901 | -2901 | 349 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1330 | 7080 |  |  | 3830 |  |  | -2901 | -2901 | 349 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1430 | 7080 |  |  | 3830 |  |  | -2901 | -2901 | 349 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1530 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1630 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1730 | 9250 |  |  | 3830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1830 | 7080 |  |  | 3830 |  |  | -4944 | -4944 | -1694 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 3500 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250421 | April | 1930 | 7080 |  |  | 5330 |  |  | -4944 | -4944 | -3203 | TTC Selection - LTTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250421 | April | 2030 | 7080 |  |  | 6830 |  |  | -4944 | -4944 | -4696 | TTC Selection - LTTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250422 | April | 330 | 9250 |  |  | 8680 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250422 | April | 530 | 9250 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | [6 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 630 | 9050 |  |  | 6531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6201 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | IT | 7010 | Foreseen violations on the border
20250422 | April | 730 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | IT | 7093 | Foreseen violations on the border
20250422 | April | 830 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | IT | 7093 | Foreseen violations on the border
20250422 | April | 930 | 9160 |  |  | 6167 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7093 | Foreseen violations on the border
20250422 | April | 1030 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1130 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1230 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250422 | April | 1330 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250422 | April | 1430 | 9160 |  |  | 5531 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250422 | April | 1530 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1630 | 9160 |  |  | 6884 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250422 | April | 1730 | 9160 |  |  | 6167 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7093 | Foreseen violations on the border
20250422 | April | 1830 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7253 | Foreseen violations on the border
20250422 | April | 1930 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7253 | Foreseen violations on the border
20250422 | April | 2030 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7253 | Foreseen violations on the border
20250422 | April | 2130 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7253 | Foreseen violations on the border
20250422 | April | 2230 | 9360 |  |  | 6727 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 7253 | Foreseen violations on the border
20250422 | April | 2330 | 8550 |  |  | 6197 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | 6610 | Foreseen violations on the border
20250423 | April | 30 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 130 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 230 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 330 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 430 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 530 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 630 | 8350 |  |  | 6912 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 730 |  | 6005 | 627 |  | 4927 | 627 | -1759 | -1759 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 103 | NA | -3673 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 830 |  | 6005 | 627 |  | 4927 | 627 | -1759 | -1759 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 203 | NA | -3673 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 930 | 6990 |  |  | 5531 |  |  | -3579 | -3579 | -1102 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1030 | 6990 |  |  | 5531 |  |  | -3579 | -3579 | -1102 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1130 | 6990 |  |  | 5531 |  |  | -3579 | -3579 | -1102 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1230 | 9160 |  |  | 6215 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7176 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1330 | 9160 |  |  | 6215 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7176 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1430 | 9160 |  |  | 6215 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2 | SI | 7176 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250423 | April | 1530 | 9160 |  |  | 7175 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1600 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1630 | 9160 |  |  | 7175 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1730 | 9160 |  |  | 7175 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1830 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 1930 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2030 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2130 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2230 | 9360 |  |  | 7775 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250423 | April | 2330 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 30 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 130 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 230 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 330 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 430 | 8550 |  |  | 7112 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
20250424 | April | 630 | 8350 |  |  | 4711 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250424 | April | 730 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2961 | Foreseen violations on the border
20250424 | April | 830 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2961 | Foreseen violations on the border
20250424 | April | 930 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2961 | Foreseen violations on the border
20250424 | April | 1030 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2961 | Foreseen violations on the border
20250424 | April | 1130 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2961 | Foreseen violations on the border
20250424 | April | 1230 | 3890 |  |  | 3211 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2961 | Foreseen violations on the border
20250424 | April | 1330 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2944 | Foreseen violations on the border
20250424 | April | 1430 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2944 | Foreseen violations on the border
20250424 | April | 1530 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2944 | Foreseen violations on the border
20250424 | April | 1630 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2944 | Foreseen violations on the border
20250424 | April | 1730 | 3975 |  |  | 3279 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [14 empty] | IT | 2944 | Foreseen violations on the border
20250424 | April | 2130 | 6696 |  |  | 5689 |  |  | 2232 | 12 | 3222 | Minimum Margin | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250425 | April | 30 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 6500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 130 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 6500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 230 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 6500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 330 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 6500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 430 | 7330 |  |  | 6830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 6500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 530 | 7330 |  |  | 6168 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp |  |  |  | CH | 6500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 630 | 7130 |  |  | 4668 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp |  |  |  | CH | 6300 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 730 | 3168 |  |  | 3168 |  |  | 8204 | 8 | 8196 | Minimum Margin | Minimum Margin | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 830 | 3168 |  |  | 3168 |  |  | 8204 | 8 | 8196 | Minimum Margin | Minimum Margin | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 930 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1030 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1130 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1230 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1330 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1430 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1530 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1630 | 3160 |  |  | 3160 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [5 empty] | CH | 4500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1730 | 6960 |  |  | 4660 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp |  |  |  | CH | 8300 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1830 | 9330 |  |  | 6160 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp |  |  |  | CH | 8500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 1930 | 9330 |  |  | 7660 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp |  |  |  | CH | 8500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2030 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 8500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2130 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 8500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2230 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 8500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250425 | April | 2330 | 9330 |  |  | 8830 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 8500 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250426 | April | 630 | 7460 |  |  | 6330 |  |  | 1525 | 0 | 2655 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 730 | 10345 |  |  | 7830 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | [9 empty] | SI | 8682 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 830 | 10345 |  |  | 9017 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 8682 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 1030 | 8309 |  |  | 7247 |  |  | 3371 | 134 | 4299 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6912 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 1130 | 8305 |  |  | 7245 |  |  | 3371 | 130 | 4301 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6910 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250426 | April | 1830 | 10345 |  |  | 9675 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250427 | April | 930 | 7360 |  |  | 8008 |  |  | -1965 | -1965 | 0 | TTC Selection - LTTC | Scheduled TTC | NA | NA | 0 | [11 empty] | SI | 7678 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250427 | April | 1030 | 7360 |  |  | 8008 |  |  | -1965 | -1965 | 0 | TTC Selection - LTTC | Scheduled TTC | NA | NA | 0 | [11 empty] | SI | 7678 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250427 | April | 1130 | 7360 |  |  | 8008 |  |  | -1965 | -1965 | 0 | TTC Selection - LTTC | Scheduled TTC | NA | NA | 0 | [11 empty] | SI | 7678 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250427 | April | 2230 | 7396 |  |  | 9030 |  |  | 2459 | 36 | 0 | Minimum Margin | Scheduled TTC | NA | NA | 0 |  |  | AT | 435
20250427 | April | 2330 | 7591 |  |  | 9030 |  |  | 2459 | 231 | 0 | Minimum Margin | Scheduled TTC | NA | NA | 0 |  |  | AT | 435
20250428 | April | 30 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 435
20250428 | April | 130 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 435
20250428 | April | 230 | 9530 |  |  | 9030 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 435
20250428 | April | 330 | 7592 |  |  | 7592 |  |  | 828 | 132 | 696 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435
20250428 | April | 430 | 7592 |  |  | 7592 |  |  | 828 | 132 | 696 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435
20250428 | April | 530 | 7592 |  |  | 7592 |  |  | 828 | 132 | 696 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 630 | 7497 |  |  | 7497 |  |  | 856 | 237 | 619 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 730 | 6286 |  |  | 6286 |  |  | 2138 | 111 | 2027 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 830 | 6348 |  |  | 6348 |  |  | 2138 | 173 | 1965 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 930 | 6370 |  |  | 6370 |  |  | 2046 | 195 | 1851 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1030 | 6363 |  |  | 6363 |  |  | 2046 | 188 | 1858 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1130 | 6351 |  |  | 6351 |  |  | 2046 | 176 | 1870 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1230 | 6611 |  |  | 6611 |  |  | -1000 | -1000 | -1000 | Critical Branch | Critical Branch | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1330 | 6611 |  |  | 6611 |  |  | -1000 | -1000 | -1000 | Critical Branch | Critical Branch | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1430 | 6611 |  |  | 6611 |  |  | -1000 | -1000 | -1000 | Critical Branch | Critical Branch | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1530 | 6355 |  |  | 6355 |  |  | 2258 | 180 | 2078 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1630 | 6321 |  |  | 6321 |  |  | 2258 | 146 | 2112 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450
20250428 | April | 1730 | 8230 |  |  | 7821 |  |  | 2279 | 255 | 2429 | Minimum Margin | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | AT | 450
20250428 | April | 1830 | 10345 |  |  | 9321 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | AT | 450
20250428 | April | 1930 | 10345 |  |  | 9845 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450
20250428 | April | 2030 | 10345 |  |  | 9845 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450
20250428 | April | 2130 | 8345 |  |  | 8345 |  |  | 1813 | 170 | 1643 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435
20250428 | April | 2230 | 8345 |  |  | 8345 |  |  | 1813 | 170 | 1643 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250428 | April | 2330 | 7520 |  |  | 7520 |  |  | 2148 | 160 | 1988 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250429 | April | 30 | 7534 |  |  | 7534 |  |  | 174 | 154 | 20 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250429 | April | 130 | 7534 |  |  | 7534 |  |  | 174 | 154 | 20 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250429 | April | 230 | 7534 |  |  | 7534 |  |  | 174 | 154 | 20 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250429 | April | 330 | 9450 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250429 | April | 430 | 9450 |  |  | 8950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250429 | April | 530 | 9450 |  |  | 8130 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 630 | 9250 |  |  | 6630 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 730 | 8586 |  |  | 7806 |  |  | 1121 | 451 | 1450 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 830 | 8586 |  |  | 7806 |  |  | 1121 | 451 | 1450 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 930 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1030 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1130 | 9160 |  |  | 6335 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1230 | 9136 |  |  | 6335 |  |  | -1759 | -1759 | 1042 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1330 | 9136 |  |  | 6335 |  |  | -1759 | -1759 | 1042 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1430 | 9136 |  |  | 6335 |  |  | -1759 | -1759 | 1042 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1530 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1630 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1730 | 6990 |  |  | 6990 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1830 | 7348 |  |  | 7348 |  |  | 3663 | 158 | 3505 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 1930 | 7348 |  |  | 7348 |  |  | 3663 | 158 | 3505 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 2030 | 7348 |  |  | 7348 |  |  | 3663 | 158 | 3505 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 450 | Reduction because NTC over thermal limit on border
20250429 | April | 2130 | 7360 |  |  | 7360 |  |  | 2976 | 170 | 2806 | Minimum Margin | Minimum Margin | NA | NA | 0 |  |  | AT | 435 | Reduction because NTC over thermal limit on border
20250430 | April | 1530 | 9160 |  |  | 9011 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250430 | April | 1830 | 10260 |  |  | 9500 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250430 | April | 1930 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [14 empty] | IT | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2030 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [14 empty] | IT | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2130 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [14 empty] | IT | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2230 | 10260 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 332 |  |  |  |  | FR | 2843 | Process fail during TSO validation phase |  |  |  | IT | 7665 | Allocation Constraint value not properly processed by Coreso
20250430 | April | 2330 | 9450 |  |  | 8000 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 332 |  |  |  |  | FR | 2843 | Process fail during TSO validation phase |  |  |  | IT | 7670 | Allocation Constraint value not properly processed by Coreso
20250501 | May | 30 |  | 6209 | 559 |  | 6149 | 559 | 2413 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -529 | NA | -5031 |  |  | AT | 332 |  |  |  |  | FR | 2843 | Process fail during TSO validation phase
20250501 | May | 130 |  | 6209 | 559 |  | 6149 | 559 | 2413 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -429 | NA | -5031 |  |  | AT | 309 |  |  |  |  | FR | 2638 | Process fail during TSO validation phase
20250501 | May | 230 |  | 6209 | 559 |  | 6149 | 559 | 2413 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -329 | NA | -5031 |  |  | AT | 309 |  |  |  |  | FR | 2638 | Process fail during TSO validation phase
20250501 | May | 330 |  | 5803 | 395 |  | 5744 | 395 | 2502 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -65 | NA | -4954 |  |  | AT | 309 |  |  |  |  | FR | 2638 | Process fail during TSO validation phase
20250501 | May | 430 |  | 5803 | 395 |  | 5744 | 395 | 2502 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 35 | NA | -4954 |  |  | AT | 306 |  |  |  |  | FR | 2610 | Process fail during TSO validation phase
20250501 | May | 530 |  | 5803 | 395 |  | 5744 | 395 | 2502 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 135 | NA | -4954 |  |  | AT | 341
20250501 | May | 630 |  | 5603 | 395 |  | 5542 | 395 | 2557 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 235 | NA | -4752 |  |  | AT | 344
20250501 | May | 730 | 6638 |  |  | 6625 |  |  | 3526 | 126 | 3413 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 382
20250501 | May | 830 | 6683 |  |  | 6666 |  |  | 3526 | 171 | 3372 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 382
20250501 | May | 930 | 7373 |  |  | 7372 |  |  | -3046 | -3046 | -3045 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 382
20250501 | May | 1030 | 7373 |  |  | 7372 |  |  | -3046 | -3046 | -3045 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 305
20250501 | May | 1130 | 7373 |  |  | 7372 |  |  | -3046 | -3046 | -3045 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 305
20250501 | May | 1230 | 5980 |  |  | 5980 |  |  | -1806 | -1806 | -1806 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 305
20250501 | May | 1330 | 5980 |  |  | 5980 |  |  | -1806 | -1806 | -1806 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 388
20250501 | May | 1430 | 5980 |  |  | 5980 |  |  | -1806 | -1806 | -1806 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 400
20250501 | May | 1530 | 7696 |  |  | 7480 |  |  | -2511 | -2511 | -2295 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250501 | May | 1630 | 7696 |  |  | 7576 |  |  | -2511 | -2511 | -2391 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 297 |  |  |  |  | FR | 2591 | Process fail during TSO validation phase
20250501 | May | 1730 | 7696 |  |  | 7529 |  |  | -2511 | -2511 | -2344 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 297 |  |  |  |  | FR | 2591 | Process fail during TSO validation phase
20250501 | May | 1830 |  | 5376 | 638 |  | 5319 | 637 | 3424 | 107 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1192 | NA | -4045 |  |  | AT | 297 |  |  |  |  | FR | 2591 | Process fail during TSO validation phase
20250501 | May | 1930 |  | 5398 | 640 |  | 5329 | 640 | 3424 | 128 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1290 | NA | -4049 |  |  | AT | 401 |  |  |  |  | FR | 3618 | Process fail during TSO validation phase
20250501 | May | 2030 |  | 5449 | 646 |  | 5353 | 645 | 3424 | 180 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1384 | NA | -4063 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3618 | Process fail during TSO validation phase
20250501 | May | 2130 |  | 7678 | 717 |  | 7303 | 717 | 1422 | 51 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1413 | NA | -5869 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3618 | Process fail during TSO validation phase
20250501 | May | 2230 |  | 7783 | 726 |  | 7694 | 726 | 1422 | 156 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1504 | NA | -6242 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250501 | May | 2330 |  | 7758 | 724 |  | 7683 | 724 | 1422 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1606 | NA | -6235 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250502 | May | 30 | 8316 |  |  | 8308 |  |  | -3710 | -3710 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250502 | May | 130 | 8316 |  |  | 8308 |  |  | -3710 | -3710 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250502 | May | 230 | 8316 |  |  | 8308 |  |  | -3710 | -3710 | -3700 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250502 | May | 330 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -570 | NA | -5831 |  |  | AT | 415
20250502 | May | 430 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -470 | NA | -5831 |  |  | AT | 415
20250502 | May | 530 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -370 | NA | -5831 |  |  | AT | 361
20250502 | May | 630 |  | 7631 | 900 |  | 7631 | 900 | -1141 | -1141 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -270 | NA | -5831 |  |  | AT | 361
20250502 | May | 730 |  | 6836 | 766 |  | 6835 | 766 | -941 | -941 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -36 | NA | -5303 |  |  | AT | 329
20250502 | May | 830 |  | 6836 | 766 |  | 6835 | 766 | -941 | -941 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 64 | NA | -5303 |  |  | AT | 329
20250502 | May | 930 | 6580 |  |  | 6579 |  |  | -2596 | -2596 | -2595 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250502 | May | 1030 | 6580 |  |  | 6579 |  |  | -2596 | -2596 | -2595 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250502 | May | 1130 | 6580 |  |  | 6579 |  |  | -2596 | -2596 | -2595 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250502 | May | 1230 | 6580 |  |  | 6579 |  |  | -2616 | -2616 | -2615 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250502 | May | 1330 | 6580 |  |  | 6579 |  |  | -2616 | -2616 | -2615 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 392
20250502 | May | 1430 | 6580 |  |  | 6579 |  |  | -2616 | -2616 | -2615 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 412
20250502 | May | 1530 | 8475 |  |  | 8079 |  |  | -2787 | -2787 | -2394 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 412
20250502 | May | 1630 | 8475 |  |  | 8474 |  |  | -2787 | -2787 | -2786 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 234 |  |  |  |  | FR | 3609 | Process fail during TSO validation phase
20250502 | May | 1730 | 8475 |  |  | 8474 |  |  | -2787 | -2787 | -2786 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 234 |  |  |  |  | FR | 3609 | Process fail during TSO validation phase
20250502 | May | 1830 |  | 7379 | 769 |  | 7332 | 769 | 2054 | 88 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1061 | NA | -5794 |  |  | AT | 234 |  |  |  |  | FR | 3609 | Process fail during TSO validation phase
20250502 | May | 1930 |  | 7373 | 768 |  | 7330 | 768 | 2054 | 82 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1162 | NA | -5794 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250502 | May | 2030 |  | 7371 | 768 |  | 7329 | 767 | 2054 | 80 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1262 | NA | -5795 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250502 | May | 2130 |  | 8818 | 766 |  | 8788 | 766 | -3741 | -3741 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1364 | NA | -7256 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250502 | May | 2230 |  | 8818 | 766 |  | 8788 | 766 | -3741 | -3741 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1464 | NA | -7256 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250502 | May | 2330 |  | 8238 | 791 |  | 8207 | 791 | -3097 | -3097 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1539 | NA | -6625 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 30 |  | 8329 | 809 |  | 8294 | 809 | -2715 | -2715 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -779 | NA | -6676 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 130 |  | 8329 | 809 |  | 8294 | 809 | -2715 | -2715 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -679 | NA | -6676 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 230 |  | 8329 | 809 |  | 8294 | 809 | -2715 | -2715 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -579 | NA | -6676 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 330 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -474 | NA | -6363 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 430 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -374 | NA | -6363 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 530 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -274 | NA | -6363 |  |  | AT | 385
20250503 | May | 630 |  | 7989 | 804 |  | 7971 | 804 | -2647 | -2647 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -174 | NA | -6363 |  |  | AT | 385
20250503 | May | 730 |  | 7353 | 660 |  | 7352 | 660 | -1475 | -1475 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 70 | NA | -6032 |  |  | AT | 339
20250503 | May | 830 |  | 7353 | 660 |  | 7352 | 660 | -1475 | -1475 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 170 | NA | -6032 |  |  | AT | 339
20250503 | May | 930 | 6806 |  |  | 6806 |  |  | -2916 | -2916 | -2915 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 339
20250503 | May | 1030 | 6806 |  |  | 6806 |  |  | -2916 | -2916 | -2915 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250503 | May | 1130 | 6806 |  |  | 6806 |  |  | -2916 | -2916 | -2915 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250503 | May | 1230 | 6580 |  |  | 6579 |  |  | -2607 | -2607 | -2606 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250503 | May | 1330 | 6580 |  |  | 6579 |  |  | -2607 | -2607 | -2606 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250503 | May | 1430 | 6580 |  |  | 6579 |  |  | -2607 | -2607 | -2606 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 329
20250503 | May | 1530 |  | 6155 | 321 |  | 6154 | 321 | -2115 | -2115 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 1209 | NA | -5512 |  |  | AT | 329
20250503 | May | 1630 |  | 6155 | 321 |  | 6154 | 321 | -2115 | -2115 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 1309 | NA | -5512 |  |  | AT | 397
20250503 | May | 1730 |  | 6155 | 321 |  | 6154 | 321 | -2115 | -2115 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Validation phase - bilateral reduction | 1409 | NA | -5512 |  |  | AT | 397
20250503 | May | 1830 |  | 7591 | 609 |  | 7591 | 609 | -1216 | -1216 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1221 | NA | -6373 |  |  | AT | 397
20250503 | May | 1930 |  | 7591 | 609 |  | 7591 | 609 | -1216 | -1216 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1321 | NA | -6373 |  |  | AT | 404
20250503 | May | 2030 |  | 7591 | 609 |  | 7591 | 609 | -1216 | -1216 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1421 | NA | -6373 |  |  | AT | 404
20250503 | May | 2130 | 8286 |  |  | 8285 |  |  | -1836 | -1836 | -1835 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 393
20250503 | May | 2230 | 8286 |  |  | 8285 |  |  | -1836 | -1836 | -1835 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250503 | May | 2330 | 7686 |  |  | 7686 |  |  | -1217 | -1217 | -1217 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 30 |  | 7902 | 730 |  | 7888 | 730 | -1420 | -1420 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -700 | NA | -6428 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 130 |  | 7902 | 730 |  | 7888 | 730 | -1420 | -1420 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -600 | NA | -6428 |  |  | AT | 209 | Reduction because NTC over thermal limit on border
20250504 | May | 230 |  | 7902 | 730 |  | 7888 | 730 | -1420 | -1420 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -500 | NA | -6428 |  |  | AT | 209 | Reduction because NTC over thermal limit on border
20250504 | May | 330 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -637 | NA | -5844 |  |  | AT | 209 | Reduction because NTC over thermal limit on border
20250504 | May | 430 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -537 | NA | -5844 |  |  | AT | 209 | Reduction because NTC over thermal limit on border
20250504 | May | 530 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -437 | NA | -5844 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 630 |  | 7738 | 967 |  | 7738 | 947 | -1117 | -1117 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -337 | NA | -5844 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 730 |  | 8168 | 787 |  | 8141 | 787 | -2489 | -2489 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -57 | NA | -6567 |  |  | AT | 397
20250504 | May | 830 |  | 8168 | 787 |  | 8141 | 787 | -2489 | -2489 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 43 | NA | -6567 |  |  | AT | 397
20250504 | May | 930 | 7770 |  |  | 7770 |  |  | -3922 | -3922 | -3922 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 397
20250504 | May | 1030 | 7770 |  |  | 7770 |  |  | -3922 | -3922 | -3922 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 371
20250504 | May | 1130 | 7770 |  |  | 7770 |  |  | -3922 | -3922 | -3922 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 371
20250504 | May | 1230 | 7218 |  |  | 7218 |  |  | -3321 | -3321 | -3321 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 371
20250504 | May | 1330 | 7218 |  |  | 7218 |  |  | -3321 | -3321 | -3321 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 212 | Reduction because NTC over thermal limit on border
20250504 | May | 1430 | 7218 |  |  | 7218 |  |  | -3321 | -3321 | -3321 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 212 | Reduction because NTC over thermal limit on border
20250504 | May | 1530 |  | 7823 | 959 |  | 7823 | 940 | -4266 | -4266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 571 | NA | -5943 |  |  | AT | 212 | Reduction because NTC over thermal limit on border
20250504 | May | 1630 |  | 7823 | 959 |  | 7823 | 940 | -4266 | -4266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 671 | NA | -5943 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 1730 |  | 7823 | 959 |  | 7823 | 940 | -4266 | -4266 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 771 | NA | -5943 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 1830 |  | 7881 | 718 |  | 7868 | 718 | -1611 | -1611 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1112 | NA | -6432 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 1930 |  | 7881 | 718 |  | 7868 | 718 | -1611 | -1611 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1212 | NA | -6432 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 2030 |  | 7881 | 718 |  | 7868 | 718 | -1611 | -1611 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1312 | NA | -6432 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 2130 |  | 7700 | 718 |  | 7696 | 718 | -776 | -776 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1412 | NA | -6260 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250504 | May | 2230 |  | 7700 | 718 |  | 7696 | 718 | -776 | -776 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1512 | NA | -6260 |  |  | AT | 185 |  |  |  |  | FR | 3447 | Process fail during TSO validation phase
20250504 | May | 2330 |  | 7700 | 718 |  | 7696 | 718 | -776 | -776 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1612 | NA | -6260 |  |  | AT | 185 |  |  |  |  | FR | 3447 | Process fail during TSO validation phase
20250505 | May | 30 |  | 6915 | 863 |  | 6888 | 862 | 76 | 50 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -833 | NA | -5164 |  |  | AT | 185 |  |  |  |  | FR | 3447 | Process fail during TSO validation phase
20250505 | May | 130 |  | 6915 | 863 |  | 6888 | 862 | 76 | 50 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -733 | NA | -5164 |  |  | AT | 190 | Reduction because NTC over thermal limit on border
20250505 | May | 230 |  | 6915 | 863 |  | 6888 | 862 | 76 | 50 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -633 | NA | -5164 |  |  | AT | 190 | Reduction because NTC over thermal limit on border
20250505 | May | 330 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -624 | NA | -5169 |  |  | AT | 190 | Reduction because NTC over thermal limit on border
20250505 | May | 430 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -524 | NA | -5169 |  |  | AT | 190 | Reduction because NTC over thermal limit on border
20250505 | May | 530 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -424 | NA | -5169 |  |  | AT | 263 |  |  |  |  | FR | 2904 | Process fail during TSO validation phase
20250505 | May | 630 |  | 7041 | 954 |  | 7041 | 936 | -1383 | -1383 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -324 | NA | -5169 |  |  | AT | 260 |  |  |  |  | FR | 2784 | Process fail during TSO validation phase
20250505 | May | 730 |  | 6474 | 116 |  | 6431 | 115 | 4192 | 87 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 614 | NA | -6201 |  |  | AT | 299
20250505 | May | 830 |  | 5574 | 116 |  | 5525 | 115 | 4438 | 87 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 714 | NA | -5295 |  |  | AT | 308
20250505 | May | 930 | 5688 |  |  | 5687 |  |  | 3916 | 8 | 3908 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 308
20250505 | May | 1030 | 5827 |  |  | 5814 |  |  | 3916 | 147 | 3782 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 299 |  |  |  |  | FR | 2709 | Process fail during TSO validation phase
20250505 | May | 1130 | 5827 |  |  | 5814 |  |  | 3916 | 147 | 3782 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 299 |  |  |  |  | FR | 2709 | Process fail during TSO validation phase
20250505 | May | 1230 |  | 5040 | 444 |  | 4979 | 443 | 3204 | 101 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 786 | NA | -4093 |  |  | AT | 299 |  |  |  |  | FR | 2709 | Process fail during TSO validation phase
20250505 | May | 1330 |  | 5024 | 442 |  | 4973 | 442 | 3204 | 85 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 888 | NA | -4089 |  |  | AT | 306
20250505 | May | 1430 |  | 5047 | 445 |  | 4982 | 444 | 3204 | 108 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 985 | NA | -4094 |  |  | AT | 311
20250505 | May | 1530 | 5800 |  |  | 5790 |  |  | 4117 | 120 | 4007 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 306
20250505 | May | 1630 | 5890 |  |  | 5870 |  |  | 4117 | 210 | 3927 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 161
20250505 | May | 1730 | 5796 |  |  | 5786 |  |  | 4117 | 116 | 4011 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 161
20250505 | May | 1830 |  | 5650 | 685 |  | 5650 | 685 | -2694 | -2694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1145 | NA | -4280 |  |  | AT | 161
20250505 | May | 1930 |  | 5650 | 685 |  | 5650 | 685 | -2694 | -2694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1245 | NA | -4280 |  |  | AT | 341
20250505 | May | 2030 |  | 5650 | 685 |  | 5650 | 685 | -2694 | -2694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1345 | NA | -4280 |  |  | AT | 341
20250505 | May | 2130 |  | 5941 | 540 |  | 5940 | 540 | -1215 | -1215 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1590 | NA | -4860 |  |  | AT | 326
20250505 | May | 2230 |  | 5941 | 540 |  | 5940 | 540 | -1215 | -1215 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1690 | NA | -4860 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250505 | May | 2330 |  | 5381 | 565 |  | 5381 | 565 | -586 | -586 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1765 | NA | -4251 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 30 |  | 7821 | 870 |  | 7748 | 870 | -2810 | -2810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -840 | NA | -6008 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 130 |  | 7821 | 870 |  | 7748 | 870 | -2810 | -2810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -740 | NA | -6008 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 230 |  | 7821 | 870 |  | 7748 | 870 | -2810 | -2810 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -640 | NA | -6008 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 330 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -534 | NA | -5793 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 430 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -434 | NA | -5793 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 530 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -334 | NA | -5793 |  |  | AT | 378
20250506 | May | 630 |  | 7578 | 864 |  | 7521 | 864 | -2451 | -2451 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -234 | NA | -5793 |  |  | AT | 378
20250506 | May | 730 | 7054 |  |  | 7053 |  |  | -998 | -998 | -997 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 310
20250506 | May | 830 | 7054 |  |  | 7053 |  |  | -998 | -998 | -997 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 311
20250506 | May | 930 | 5876 |  |  | 5867 |  |  | 3798 | 196 | 3611 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 308
20250506 | May | 1030 | 5882 |  |  | 5870 |  |  | 3798 | 202 | 3608 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 395
20250506 | May | 1130 | 5835 |  |  | 5828 |  |  | 3798 | 155 | 3650 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250506 | May | 1230 | 8034 |  |  | 7328 |  |  | 1295 | 122 | 1851 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 393
20250506 | May | 1330 | 8034 |  |  | 8015 |  |  | 1295 | 122 | 1184 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 306
20250506 | May | 1430 | 8034 |  |  | 7288 |  |  | 1295 | 122 | 1890 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 308
20250506 | May | 1530 | 5797 |  |  | 5788 |  |  | 3647 | 117 | 3539 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 310
20250506 | May | 1630 | 5839 |  |  | 5826 |  |  | 3647 | 159 | 3501 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 372
20250506 | May | 1730 | 5870 |  |  | 5854 |  |  | 3647 | 190 | 3473 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 368
20250506 | May | 1830 |  | 6432 | 594 |  | 6431 | 594 | 1662 | 154 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1236 | NA | -5243 |  |  | AT | 371
20250506 | May | 1930 |  | 6370 | 588 |  | 6369 | 588 | 1662 | 92 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1342 | NA | -5193 |  |  | AT | 411
20250506 | May | 2030 |  | 6414 | 592 |  | 6414 | 592 | 1662 | 136 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1438 | NA | -5230 |  |  | AT | 411
20250506 | May | 2130 |  | 7066 | 642 |  | 7036 | 639 | -2017 | -2017 | 0 | Critical Branch | Validation phase | 1488 | NA | -5758 |  |  | AT | 399
20250506 | May | 2230 |  | 7066 | 642 |  | 7036 | 639 | -2017 | -2017 | 0 | Critical Branch | Validation phase | 1588 | NA | -5758 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250506 | May | 2330 |  | 6490 | 667 |  | 6475 | 666 | -1358 | -1358 | 0 | Critical Branch | Validation phase | 1663 | NA | -5143 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250507 | May | 30 |  | 7277 | 812 |  | 7240 | 812 | -2000 | -2000 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -782 | NA | -5616 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250507 | May | 130 |  | 7277 | 812 |  | 7240 | 812 | -2000 | -2000 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -682 | NA | -5616 |  |  | AT | 404
20250507 | May | 230 |  | 7277 | 812 |  | 7240 | 812 | -2000 | -2000 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -582 | NA | -5616 |  |  | AT | 404
20250507 | May | 330 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -347 | NA | -5213 |  |  | AT | 404
20250507 | May | 430 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -247 | NA | -5213 |  |  | AT | 404
20250507 | May | 530 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -147 | NA | -5213 |  |  | AT | 404
20250507 | May | 630 |  | 6568 | 677 |  | 6567 | 677 | -3900 | -3900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -47 | NA | -5213 |  |  | AT | 347
20250507 | May | 730 |  | 6957 | 705 |  | 6956 | 705 | -1703 | -1703 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 25 | NA | -5546 |  |  | AT | 365
20250507 | May | 830 |  | 6897 | 705 |  | 6896 | 705 | -1641 | -1641 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 125 | NA | -5486 |  |  | AT | 365
20250507 | May | 930 | 7790 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 337
20250507 | May | 1030 | 7790 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 262
20250507 | May | 1130 | 7790 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 262
20250507 | May | 1230 | 5746 |  |  | 5737 |  |  | 2761 | 126 | 2644 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 262
20250507 | May | 1330 | 5746 |  |  | 5737 |  |  | 2761 | 126 | 2644 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 263 |  |  |  |  | FR | 2699 | Process fail during TSO validation phase
20250507 | May | 1430 | 5746 |  |  | 5737 |  |  | 2761 | 126 | 2644 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 306 |  |  |  |  | FR | 2708 | Process fail during TSO validation phase
20250507 | May | 1530 |  | 5326 | 337 |  | 5258 | 337 | 2382 | 119 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1193 | NA | -4584 |  |  | AT | 306 |  |  |  |  | FR | 2708 | Process fail during TSO validation phase
20250507 | May | 1630 |  | 5386 | 337 |  | 5317 | 337 | 2355 | 119 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1293 | NA | -4643 |  |  | AT | 359
20250507 | May | 1730 |  | 5386 | 337 |  | 5317 | 337 | 2355 | 119 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1393 | NA | -4643 |  |  | AT | 350
20250507 | May | 1830 |  | 6237 | 587 |  | 6236 | 587 | 2602 | 396 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1243 | NA | -5062 |  |  | AT | 339
20250507 | May | 1930 |  | 6087 | 573 |  | 6086 | 573 | 2602 | 246 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1357 | NA | -4940 |  |  | AT | 414
20250507 | May | 2030 |  | 5913 | 558 |  | 5912 | 558 | 2602 | 72 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1472 | NA | -4796 |  |  | AT | 417
20250507 | May | 2130 |  | 7106 | 690 |  | 7106 | 690 | 1946 | 335 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1440 | NA | -5726 |  |  | AT | 404
20250507 | May | 2230 |  | 7164 | 695 |  | 7163 | 695 | 1946 | 393 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1535 | NA | -5773 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3612 | Process fail during TSO validation phase
20250507 | May | 2330 |  | 6584 | 720 |  | 6576 | 720 | 2495 | 393 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1610 | NA | -5136 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3612 | Process fail during TSO validation phase
20250508 | May | 30 |  | 7777 | 727 |  | 7686 | 727 | 2163 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -697 | NA | -6232 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3612 | Process fail during TSO validation phase
20250508 | May | 130 |  | 7777 | 727 |  | 7686 | 727 | 2163 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -597 | NA | -6232 |  |  | AT | 371
20250508 | May | 230 |  | 7777 | 727 |  | 7686 | 727 | 2163 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -497 | NA | -6232 |  |  | AT | 371
20250508 | May | 330 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -360 | NA | -5499 |  |  | AT | 371
20250508 | May | 430 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -260 | NA | -5499 |  |  | AT | 371
20250508 | May | 530 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -160 | NA | -5499 |  |  | AT | 372
20250508 | May | 630 |  | 6880 | 690 |  | 6879 | 690 | -2425 | -2425 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -60 | NA | -5499 |  |  | AT | 372
20250508 | May | 730 |  | 7235 | 625 |  | 7234 | 625 | -3196 | -3196 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 105 | NA | -5984 |  |  | AT | 324
20250508 | May | 830 |  | 7235 | 625 |  | 7234 | 625 | -3196 | -3196 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 205 | NA | -5984 |  |  | AT | 321
20250508 | May | 930 | 6799 |  |  | 6250 |  |  | 3249 | 219 | 3579 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1030 | 6740 |  |  | 6250 |  |  | 3249 | 160 | 3579 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1130 | 6740 |  |  | 6250 |  |  | 3249 | 160 | 3579 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1230 | 6741 |  |  | 6250 |  |  | 4029 | 161 | 4359 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1330 | 6741 |  |  | 6250 |  |  | 4029 | 161 | 4359 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1430 | 6741 |  |  | 6250 |  |  | 4029 | 161 | 4359 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1530 | 6743 |  |  | 6250 |  |  | 3332 | 163 | 3662 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 321
20250508 | May | 1630 | 6739 |  |  | 6250 |  |  | 3332 | 159 | 3662 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 313
20250508 | May | 1730 | 6739 |  |  | 6250 |  |  | 3332 | 159 | 3662 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 313
20250508 | May | 1830 |  | 6154 | 469 |  | 6085 | 463 | -1598 | -1598 | 0 | TTC Selection - LTTCImport | Validation phase | 1361 | NA | -5159 |  |  | AT | 313
20250508 | May | 1930 |  | 6154 | 469 |  | 6085 | 463 | -1598 | -1598 | 0 | TTC Selection - LTTCImport | Validation phase | 1461 | NA | -5159 |  |  | AT | 369
20250508 | May | 2030 |  | 6154 | 469 |  | 6085 | 463 | -1598 | -1598 | 0 | TTC Selection - LTTCImport | Validation phase | 1561 | NA | -5159 |  |  | AT | 369
20250508 | May | 2130 |  | 7175 | 614 |  | 7175 | 614 | -2469 | -2469 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1516 | NA | -5947 |  |  | AT | 355
20250508 | May | 2230 |  | 7175 | 614 |  | 7175 | 614 | -2469 | -2469 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1616 | NA | -5947 |  |  | AT | 413
20250508 | May | 2330 |  | 6595 | 639 |  | 6595 | 639 | -1823 | -1823 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1691 | NA | -5317 |  |  | AT | 413
20250509 | May | 30 |  | 7593 | 684 |  | 7593 | 684 | -2597 | -2597 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -654 | NA | -6225 |  |  | AT | 413
20250509 | May | 130 |  | 7593 | 684 |  | 7593 | 684 | -2597 | -2597 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -554 | NA | -6225 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250509 | May | 230 |  | 7593 | 684 |  | 7593 | 684 | -2597 | -2597 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -454 | NA | -6225 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250509 | May | 330 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -360 | NA | -6274 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250509 | May | 430 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -260 | NA | -6274 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250509 | May | 530 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -160 | NA | -6274 |  |  | AT | 368
20250509 | May | 630 |  | 7656 | 690 |  | 7654 | 690 | -2243 | -2243 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -60 | NA | -6274 |  |  | AT | 377
20250509 | May | 730 |  | 7164 | 594 |  | 7163 | 594 | 1295 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 136 | NA | -5975 |  |  | AT | 369
20250509 | May | 830 |  | 7316 | 606 |  | 7315 | 606 | 1295 | 152 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 224 | NA | -6103 |  |  | AT | 366
20250509 | May | 930 | 7665 |  |  | 7645 |  |  | 5361 | 213 | 5168 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 365
20250509 | May | 1030 | 7619 |  |  | 7604 |  |  | 5361 | 167 | 5209 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 405
20250509 | May | 1130 | 7603 |  |  | 7590 |  |  | 5361 | 151 | 5223 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 405
20250509 | May | 1230 |  | 7825 | 680 |  | 7824 | 680 | -1900 | -1900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 550 | NA | -6464 |  |  | AT | 405
20250509 | May | 1330 |  | 7825 | 680 |  | 7824 | 680 | -1900 | -1900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 650 | NA | -6464 |  |  | AT | 416 |  |  |  |  | FR | 3704 | Process fail during TSO validation phase
20250509 | May | 1430 |  | 7825 | 680 |  | 7824 | 680 | -1900 | -1900 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 750 | NA | -6464 |  |  | AT | 416 |  |  |  |  | FR | 3704 | Process fail during TSO validation phase
20250509 | May | 1530 |  | 8035 | 646 |  | 7968 | 646 | 3037 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 884 | NA | -6676 |  |  | AT | 453 |  |  |  |  | FR | 3736 | Process fail during TSO validation phase
20250509 | May | 1630 |  | 8035 | 646 |  | 7968 | 646 | 3037 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 984 | NA | -6676 |  |  | AT | 378
20250509 | May | 1730 |  | 8165 | 646 |  | 7656 | 646 | 2965 | 132 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1084 | NA | -6364 |  |  | AT | 378
20250509 | May | 1830 |  | 6219 | 489 |  | 6219 | 489 | -3067 | -3067 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1341 | NA | -5241 |  |  | AT | 378
20250509 | May | 1930 |  | 6219 | 489 |  | 6219 | 489 | -3067 | -3067 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1441 | NA | -5241 |  |  | AT | 378
20250509 | May | 2030 |  | 6219 | 489 |  | 6219 | 489 | -3067 | -3067 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1541 | NA | -5241 |  |  | AT | 378
20250509 | May | 2130 |  | 6219 | 429 |  | 6219 | 429 | -2544 | -2544 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1701 | NA | -5361 |  |  | AT | 357
20250509 | May | 2230 |  | 6219 | 429 |  | 6219 | 429 | -2544 | -2544 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1801 | NA | -5361 |  |  | AT | 468
20250509 | May | 2330 |  | 5649 | 454 |  | 5649 | 454 | -1923 | -1923 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1876 | NA | -4741 |  |  | AT | 468
20250510 | May | 30 |  | 7579 | 690 |  | 7209 | 657 | -2251 | -2251 | 0 | Critical Branch | Validation phase | -660 | NA | -5895 |  |  | AT | 468
20250510 | May | 130 |  | 7579 | 690 |  | 7209 | 657 | -2251 | -2251 | 0 | Critical Branch | Validation phase | -560 | NA | -5895 |  |  | AT | 475 | Reduction because NTC over thermal limit on border
20250510 | May | 230 |  | 7579 | 690 |  | 7209 | 657 | -2251 | -2251 | 0 | Critical Branch | Validation phase | -460 | NA | -5895 |  |  | AT | 475 | Reduction because NTC over thermal limit on border
20250510 | May | 330 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | -489 | NA | -6764 |  |  | AT | 475 | Reduction because NTC over thermal limit on border
20250510 | May | 430 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | -389 | NA | -6764 |  |  | AT | 475 | Reduction because NTC over thermal limit on border
20250510 | May | 530 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | -289 | NA | -6764 |  |  | AT | 483
20250510 | May | 630 |  | 8611 | 819 |  | 8366 | 801 | -3598 | -3598 | 0 | Critical Branch | Validation phase | -189 | NA | -6764 |  |  | AT | 483
20250510 | May | 730 |  | 8123 | 700 |  | 8123 | 700 | -2557 | -2557 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 30 | NA | -6723 |  |  | AT | 424
20250510 | May | 830 |  | 8123 | 700 |  | 8123 | 700 | -2557 | -2557 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 130 | NA | -6723 |  |  | AT | 424
20250510 | May | 930 | 7535 |  |  | 7535 |  |  | -4021 | -4021 | -4020 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 424
20250510 | May | 1030 | 7535 |  |  | 7535 |  |  | -4021 | -4021 | -4020 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 378
20250510 | May | 1130 | 7535 |  |  | 7535 |  |  | -4021 | -4021 | -4020 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 378
20250510 | May | 1230 | 6645 |  |  | 6645 |  |  | -1103 | -1103 | -1103 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 378
20250510 | May | 1330 | 6645 |  |  | 6645 |  |  | -1103 | -1103 | -1103 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 423
20250510 | May | 1430 | 6645 |  |  | 6645 |  |  | -1103 | -1103 | -1103 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 423
20250510 | May | 1530 | 7523 |  |  | 7523 |  |  | -2299 | -2299 | -2299 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 423
20250510 | May | 1630 | 7523 |  |  | 7523 |  |  | -2299 | -2299 | -2299 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450
20250510 | May | 1730 | 7523 |  |  | 7523 |  |  | -2299 | -2299 | -2299 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 450
20250510 | May | 1830 |  | 7531 | 599 |  | 7531 | 599 | -2307 | -2307 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1231 | NA | -6333 |  |  | AT | 450
20250510 | May | 1930 |  | 7531 | 599 |  | 7531 | 599 | -2307 | -2307 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1331 | NA | -6333 |  |  | AT | 461
20250510 | May | 2030 |  | 7531 | 599 |  | 7531 | 599 | -2307 | -2307 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1431 | NA | -6333 |  |  | AT | 461
20250510 | May | 2130 | 8269 |  |  | 8268 |  |  | -2429 | -2429 | -2428 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 445
20250510 | May | 2230 | 8269 |  |  | 8268 |  |  | -2429 | -2429 | -2428 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250510 | May | 2330 | 7664 |  |  | 7664 |  |  | -1811 | -1811 | -1810 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250511 | May | 30 |  | 8518 | 787 |  | 8473 | 787 | -2896 | -2896 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -757 | NA | -6899 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250511 | May | 130 |  | 8518 | 787 |  | 8473 | 787 | -2896 | -2896 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -657 | NA | -6899 |  |  | AT | 356 |  |  |  |  | FR | 2923 | Process fail during TSO validation phase
20250511 | May | 230 |  | 8518 | 787 |  | 8043 | 787 | -2896 | -2896 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -557 | NA | -6469 |  |  | AT | 356 |  |  |  |  | FR | 2923 | Process fail during TSO validation phase
20250511 | May | 330 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -1779 | NA | 677 |  |  | AT | 356 |  |  |  |  | FR | 2923 | Process fail during TSO validation phase
20250511 | May | 430 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -1679 | NA | 677 |  |  | AT | 356 |  |  |  |  | FR | 2923 | Process fail during TSO validation phase
20250511 | May | 530 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -1579 | NA | 677 |  |  | AT | 415
20250511 | May | 630 |  | 3641 | 2109 |  | 3541 | 2109 | 1179 | 109 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -1479 | NA | 677 |  |  | AT | 415
20250511 | May | 730 | 8150 |  |  | 8150 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 371
20250511 | May | 830 | 8150 |  |  | 8150 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 371
20250511 | May | 930 | 7222 |  |  | 7221 |  |  | -952 | -952 | -951 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 371
20250511 | May | 1030 | 7222 |  |  | 7221 |  |  | -952 | -952 | -951 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 340
20250511 | May | 1130 | 7222 |  |  | 7221 |  |  | -952 | -952 | -951 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 340
20250511 | May | 1230 | 6563 |  |  | 6562 |  |  | -939 | -939 | -939 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 340
20250511 | May | 1330 | 6563 |  |  | 6562 |  |  | -939 | -939 | -939 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250511 | May | 1430 | 6563 |  |  | 6562 |  |  | -939 | -939 | -939 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250511 | May | 1530 | 6923 |  |  | 6922 |  |  | -3373 | -3373 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250511 | May | 1630 | 6923 |  |  | 6922 |  |  | -3373 | -3373 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 401 |  |  |  |  | FR | 3474 | Process fail during TSO validation phase
20250511 | May | 1730 | 6923 |  |  | 6922 |  |  | -3373 | -3373 | -3373 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 401 |  |  |  |  | FR | 3474 | Process fail during TSO validation phase
20250511 | May | 1830 |  | 7351 | 663 |  | 7347 | 663 | 1319 | 8 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1167 | NA | -6021 |  |  | AT | 401 |  |  |  |  | FR | 3474 | Process fail during TSO validation phase
20250511 | May | 1930 |  | 7353 | 663 |  | 7347 | 663 | 1319 | 10 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1267 | NA | -6021 |  |  | AT | 394
20250511 | May | 2030 |  | 7353 | 663 |  | 7347 | 663 | 1319 | 10 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1367 | NA | -6021 |  |  | AT | 394
20250511 | May | 2130 |  | 7218 | 650 |  | 7217 | 650 | -132 | -132 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1480 | NA | -5917 |  |  | AT | 394
20250512 | May | 30 |  | 5358 | 496 |  | 5358 | 496 | -1354 | -1354 | 0 | TTC Selection - LTTCImport and LTTCExport | TTC Selection - LTTCImport and LTTCExport | -466 | NA | -4366
20250512 | May | 930 | 7695 |  |  | 7630 |  |  | -2107 | -2107 | -2042 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250512 | May | 1130 | 7695 |  |  | 7630 |  |  | -2107 | -2107 | -2042 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250512 | May | 1230 | 6130 |  |  | 6130 |  |  | -2446 | -2446 | -2446 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1330 | 6130 |  |  | 6130 |  |  | -2446 | -2446 | -2446 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1430 | 6130 |  |  | 6130 |  |  | -2446 | -2446 | -2446 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1530 | 7268 |  |  | 7268 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1630 | 7268 |  |  | 7268 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1730 | 7268 |  |  | 7268 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250512 | May | 1830 | 6306 |  |  | 6305 |  |  | 5135 | 26 | 5110 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6055 | Reduction due to missing redispatch potential
20250512 | May | 2130 | 7869 |  |  | 7791 |  |  | 5707 | 9 | 5776 | Minimum Margin | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250512 | May | 2330 | 7422 |  |  | 7412 |  |  | 6037 | 162 | 5885 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7162 | Reduction due to missing redispatch potential
20250513 | May | 130 | 5891 |  |  | 5878 |  |  | 2714 | 111 | 2616 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250513 | May | 230 | 5891 |  |  | 5878 |  |  | 2714 | 111 | 2616 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250513 | May | 330 |  | 5506 | 394 |  | 5445 | 394 | 1427 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -64 | NA | -4657 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250513 | May | 430 |  | 5506 | 394 |  | 5445 | 394 | 1427 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 36 | NA | -4657 | [8 empty] | FR | 2568 | Process fail during TSO validation phase
20250513 | May | 930 | 8300 |  |  | 7868 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250513 | May | 1130 | 8300 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250514 | May | 930 | 8125 |  |  | 7563 |  |  | 2267 | 176 | 2653 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7313 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1030 | 8106 |  |  | 7563 |  |  | 2267 | 157 | 2653 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7313 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1130 | 8106 |  |  | 7563 |  |  | 2267 | 157 | 2653 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7313 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1530 | 8142 |  |  | 7568 |  |  | -1893 | -1893 | -1319 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7318 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1630 | 8142 |  |  | 7568 |  |  | -1893 | -1893 | -1319 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7318 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 1730 | 8142 |  |  | 7568 |  |  | -1893 | -1893 | -1319 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7318 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250514 | May | 2230 |  | 6282 | 477 |  | 6282 | 477 | 1972 | 423 | 0 | Minimum Margin | Minimum Margin | 1753 | NA | -5328 | [8 empty] | FR | 2810 | Process fail during TSO validation phase
20250514 | May | 2330 |  | 5438 | 479 |  | 5436 | 479 | 2538 | 140 | 0 | Minimum Margin | Minimum Margin | 1851 | NA | -4478 | [8 empty] | FR | 2810 | Process fail during TSO validation phase
20250515 | May | 30 |  | 6247 | 588 |  | 6007 | 588 | 900 | 454 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -558 | NA | -4831 | [8 empty] | FR | 2810 | Process fail during TSO validation phase
20250515 | May | 130 |  | 6247 | 588 |  | 6007 | 588 | 900 | 454 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -458 | NA | -4831 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250515 | May | 230 |  | 6247 | 588 |  | 6007 | 588 | 900 | 454 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -358 | NA | -4831 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250515 | May | 330 |  | 5507 | 503 |  | 5446 | 503 | 2334 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -173 | NA | -4440 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250515 | May | 430 |  | 5507 | 503 |  | 5446 | 503 | 2334 | 116 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -73 | NA | -4440 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250515 | May | 930 | 6454 |  |  | 6442 |  |  | 4420 | 174 | 4258 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6192 | Reduction due to missing redispatch potential
20250515 | May | 1030 | 6437 |  |  | 6427 |  |  | 4420 | 157 | 4273 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6177 | Reduction due to missing redispatch potential
20250515 | May | 1130 | 6437 |  |  | 6427 |  |  | 4420 | 157 | 4273 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6177 | Reduction due to missing redispatch potential
20250515 | May | 1830 | 6444 |  |  | 6435 |  |  | 3623 | 164 | 3468 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6185 | Reduction due to missing redispatch potential
20250515 | May | 1930 | 6444 |  |  | 6435 |  |  | 3623 | 164 | 3468 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6185 | Reduction due to missing redispatch potential
20250515 | May | 2030 | 6444 |  |  | 6435 |  |  | 3623 | 164 | 3468 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6185 | Reduction due to missing redispatch potential
20250516 | May | 130 | 6931 |  |  | 6921 |  |  | 2091 | 145 | 1956 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250516 | May | 230 | 6931 |  |  | 6921 |  |  | 2091 | 145 | 1956 | Minimum Margin | Validation phase | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250516 | May | 330 |  | 5535 | 482 |  | 5459 | 482 | 2132 | 144 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -152 | NA | -4495 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250516 | May | 430 |  | 5535 | 482 |  | 5459 | 482 | 2132 | 144 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -52 | NA | -4495 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250516 | May | 2130 |  | 8025 | 655 |  | 7948 | 655 | -2086 | -2086 | 0 | Critical Branch | Smoothing ramp | 1475 | NA | -6638 | Smoothing | Smoothing ramp
20250516 | May | 2230 |  | 8025 | 655 |  | 8025 | 655 | -2086 | -2086 | 0 | Critical Branch | Min import NTC Threshold | 1575 | NA | -6715 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250516 | May | 2330 |  | 7445 | 680 |  | 7445 | 680 | -1493 | -1493 | 0 | Critical Branch | Min import NTC Threshold | 1650 | NA | -6085 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250517 | May | 30 |  | 5888 | 426 |  | 5786 | 426 | 1412 | 201 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -396 | NA | -4934 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250517 | May | 130 |  | 5885 | 426 |  | 5785 | 426 | 1412 | 197 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -296 | NA | -4933 | [8 empty] | FR | 3498
20250517 | May | 230 |  | 5859 | 423 |  | 5772 | 423 | 1412 | 172 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -193 | NA | -4926 | [8 empty] | FR | 3498
20250517 | May | 330 | 8150 |  |  | 7665 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 3498
20250517 | May | 430 | 8150 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 3498
20250517 | May | 530 | 8150 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 3727
20250517 | May | 630 | 8150 |  |  | 8031 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 3727
20250517 | May | 730 | 8750 |  |  | 8633 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2832 | Process fail during TSO validation phase
20250517 | May | 830 | 8750 |  |  | 8183 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2832 | Process fail during TSO validation phase
20250517 | May | 930 |  | 6362 | 400 |  | 6258 | 400 | 3346 | 208 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 530 | NA | -5458 | [8 empty] | FR | 2832 | Process fail during TSO validation phase
20250517 | May | 1030 |  | 6298 | 395 |  | 6225 | 395 | 3346 | 143 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 635 | NA | -5435 | [8 empty] | FR | 3452
20250517 | May | 1130 |  | 6298 | 395 |  | 6225 | 395 | 3346 | 143 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 735 | NA | -5435 | [8 empty] | FR | 3452
20250517 | May | 1230 | 8160 |  |  | 7025 |  |  | -2079 | -2079 | -944 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 6775 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 3452
20250517 | May | 1330 | 8160 |  |  | 7025 |  |  | -2079 | -2079 | -944 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 6775 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 2716 | Process fail during TSO validation phase
20250517 | May | 1430 | 8160 |  |  | 7025 |  |  | -2079 | -2079 | -944 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 6775 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | FR | 2716 | Process fail during TSO validation phase
20250517 | May | 1530 | 6788 |  |  | 6565 |  |  | 5936 | 208 | 6173 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6521 | Reduction due to missing redispatch potential | FR | 2716 | Process fail during TSO validation phase
20250517 | May | 1630 | 6785 |  |  | 6563 |  |  | 5936 | 205 | 6173 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6518 | Reduction due to missing redispatch potential | FR | 2716 | Process fail during TSO validation phase
20250517 | May | 1730 | 6739 |  |  | 6542 |  |  | 5936 | 159 | 6174 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6477 | Reduction due to missing redispatch potential | FR | 2716 | Process fail during TSO validation phase
20250517 | May | 1830 | 6738 |  |  | 6541 |  |  | 1866 | 158 | 2105 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6475 | Reduction due to missing redispatch potential | FR | 2716
20250517 | May | 1930 | 6789 |  |  | 6566 |  |  | 1866 | 209 | 2104 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6522 | Reduction due to missing redispatch potential | FR | 2832 | Process fail during TSO validation phase
20250517 | May | 2030 | 6580 |  |  | 6463 |  |  | 1866 | 0 | 2109 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 2832 | Process fail during TSO validation phase
20250517 | May | 2130 |  | 6289 | 389 |  | 6221 | 389 | 2666 | 135 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1741 | NA | -5443 | [8 empty] | FR | 2591 | Process fail during TSO validation phase
20250518 | May | 30 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 130 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 230 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 330 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 430 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 530 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 630 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 730 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 830 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 930 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1030 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1130 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1230 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1330 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1430 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1530 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1630 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1730 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1830 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 1930 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 2030 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 2130 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20250518 | May | 2230 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7405 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | FR | 2638 | Process fail during TSO validation phase
20250518 | May | 2330 | 8150 |  |  | 7650 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [5 empty] | CH | 7400 | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | FR | 2638 | Process fail during TSO validation phase
20250519 | May | 30 |  | 5743 | 464 |  | 5715 | 464 | 1402 | 55 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -434 | NA | -4787 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250519 | May | 130 |  | 5743 | 464 |  | 5715 | 464 | 1402 | 55 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -334 | NA | -4787 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250519 | May | 230 |  | 5743 | 464 |  | 5715 | 464 | 1402 | 55 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -234 | NA | -4787 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250519 | May | 330 |  | 5816 | 394 |  | 5751 | 394 | 1899 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -64 | NA | -4963 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250519 | May | 430 |  | 5816 | 394 |  | 5751 | 394 | 1899 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 36 | NA | -4963 | [8 empty] | FR | 2638 | Process fail during TSO validation phase
20250519 | May | 730 | 6393 |  |  | 6250 |  |  | 5708 | 113 | 5738 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 830 | 6512 |  |  | 6250 |  |  | 5708 | 232 | 5738 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 930 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1030 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1130 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1230 | 6446 |  |  | 6250 |  |  | 6550 | 166 | 6580 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1330 | 6446 |  |  | 6250 |  |  | 6550 | 166 | 6580 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1430 | 6446 |  |  | 6250 |  |  | 6550 | 166 | 6580 | Minimum Margin | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1530 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1630 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250519 | May | 1730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 130 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250520 | May | 230 | 7850 |  |  | 7356 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | [6 empty] | FR | 2598 | Process fail during TSO validation phase
20250520 | May | 330 |  | 5553 | 398 |  | 5467 | 398 | 2250 | 162 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -68 | NA | -4671 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250520 | May | 430 |  | 5492 | 393 |  | 5439 | 393 | 2250 | 100 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 37 | NA | -4653 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250520 | May | 730 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 830 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 930 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1030 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1130 | 8300 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1530 | 8300 |  |  | 6509 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6259 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1630 | 8300 |  |  | 6509 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6259 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250520 | May | 1730 | 8300 |  |  | 6509 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6259 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 530 | 7850 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250521 | May | 630 | 7850 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 830 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 930 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1030 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1130 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1230 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6333 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1330 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6333 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1430 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6333 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1530 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1630 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250521 | May | 1830 | 8450 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250522 | May | 530 | 7850 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250522 | May | 630 | 7850 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 830 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 930 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1030 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1130 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1230 | 8390 |  |  | 6553 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6303 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1330 | 8390 |  |  | 6553 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6303 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1430 | 8390 |  |  | 6553 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6303 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1530 | 8390 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1630 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250522 | May | 1830 | 8450 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250522 | May | 2230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250522 | May | 2330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250523 | May | 30 |  | 5541 | 397 |  | 5462 | 397 | 3341 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -367 | NA | -4668 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250523 | May | 130 |  | 5541 | 397 |  | 5462 | 397 | 3341 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -267 | NA | -4668 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250523 | May | 230 |  | 5541 | 397 |  | 5462 | 397 | 3341 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -167 | NA | -4668 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250523 | May | 330 |  | 5542 | 447 |  | 5462 | 447 | 3095 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -117 | NA | -4568 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250523 | May | 430 |  | 5542 | 447 |  | 5462 | 447 | 3095 | 150 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -17 | NA | -4568 | [8 empty] | FR | 2598 | Process fail during TSO validation phase
20250523 | May | 730 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 830 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 930 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1030 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1130 | 8450 |  |  | 6250 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1230 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6333 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1330 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6333 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1430 | 8450 |  |  | 6583 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6333 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1530 | 6280 |  |  | 6250 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1630 | 6280 |  |  | 6250 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1730 | 6580 |  |  | 6250 |  |  | 0 | 0 | 0 | TTC Selection - LTTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 6000 | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250523 | May | 1830 | 8750 |  |  | 7750 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250523 | May | 1930 | 8750 |  |  | 8750 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 | [8 empty] | FR | 2832 | Process fail during TSO validation phase
20250523 | May | 2030 | 8750 |  |  | 8154 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | [6 empty] | FR | 2832 | Process fail during TSO validation phase
20250523 | May | 2130 |  | 6303 | 441 |  | 6228 | 441 | 5105 | 149 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1689 | NA | -5346 | [8 empty] | FR | 2591 | Process fail during TSO validation phase
20250524 | May | 130 | 6104 |  |  | 6101 |  |  | 2012 | 24 | 1991 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5851 | Reduction due to missing redispatch potential
20250524 | May | 230 | 6264 |  |  | 6237 |  |  | 2012 | 184 | 1855 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5987 | Reduction due to missing redispatch potential
20250524 | May | 330 | 6241 |  |  | 6229 |  |  | 1697 | 161 | 1548 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5979 | Reduction due to missing redispatch potential
20250524 | May | 430 | 6241 |  |  | 6229 |  |  | 1697 | 161 | 1548 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5979 | Reduction due to missing redispatch potential
20250524 | May | 530 | 6283 |  |  | 6268 |  |  | 1697 | 203 | 1509 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6018 | Reduction due to missing redispatch potential | FR | 2832 | Process fail during TSO validation phase
20250524 | May | 630 | 6080 |  |  | 6080 |  |  | 1697 | 0 | 1697 | TTC Selection - LTTC | TTC Selection - LTTC | NA | NA | 0 | [8 empty] | FR | 2832 | Process fail during TSO validation phase
20250524 | May | 930 | 7952 |  |  | 7945 |  |  | 3421 | 74 | 3354 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7695 | Reduction due to missing redispatch potential
20250524 | May | 1030 | 8026 |  |  | 8012 |  |  | 3421 | 148 | 3287 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7762 | Reduction due to missing redispatch potential
20250524 | May | 1130 | 8026 |  |  | 8012 |  |  | 3421 | 148 | 3287 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 7762 | Reduction due to missing redispatch potential
20250524 | May | 1530 | 6795 |  |  | 6774 |  |  | 4432 | 215 | 4238 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6524 | Reduction due to missing redispatch potential
20250524 | May | 1630 | 6728 |  |  | 6714 |  |  | 4432 | 148 | 4298 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6464 | Reduction due to missing redispatch potential
20250524 | May | 1730 | 6737 |  |  | 6722 |  |  | 4432 | 157 | 4290 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6472 | Reduction due to missing redispatch potential
20250524 | May | 1930 | 6809 |  |  | 6788 |  |  | 1804 | 229 | 1596 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6538 | Reduction due to missing redispatch potential
20250524 | May | 2130 |  | 8069 | 650 |  | 7802 | 650 | -1901 | -1901 | 0 | Critical Branch | Smoothing ramp | 1480 | NA | -6502 | Smoothing | Smoothing ramp
20250524 | May | 2230 |  | 8069 | 650 |  | 8069 | 650 | -1901 | -1901 | 0 | Critical Branch | Critical Branch | 1580 | NA | -6769 |  |  | AT | 308
20250524 | May | 2330 |  | 7489 | 675 |  | 7489 | 675 | -1262 | -1262 | 0 | Critical Branch | Critical Branch | 1655 | NA | -6139 |  |  | AT | 308
20250525 | May | 30 |  | 5781 | 521 |  | 5781 | 521 | -508 | -508 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -491 | NA | -4739 |  |  | AT | 308
20250525 | May | 130 |  | 5781 | 521 |  | 5781 | 521 | -508 | -508 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -391 | NA | -4739 |  |  | AT | 403
20250525 | May | 230 |  | 5781 | 521 |  | 5781 | 521 | -508 | -508 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -291 | NA | -4739 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 330 |  | 7718 | 695 |  | 7421 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -365 | NA | -6031 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 430 |  | 7718 | 695 |  | 7713 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -265 | NA | -6323 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 530 |  | 7718 | 695 |  | 7713 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -165 | NA | -6323 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 630 |  | 7718 | 695 |  | 7713 | 695 | -1805 | -1805 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -65 | NA | -6323 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 730 |  | 8443 | 774 |  | 8395 | 774 | -1909 | -1909 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -44 | NA | -6847 |  |  | AT | 393
20250525 | May | 830 |  | 8443 | 774 |  | 8395 | 774 | -1909 | -1909 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 56 | NA | -6847 |  |  | AT | 393
20250525 | May | 930 | 7762 |  |  | 7761 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 393
20250525 | May | 1030 | 7762 |  |  | 7761 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 414
20250525 | May | 1130 | 7762 |  |  | 7761 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 414
20250525 | May | 1230 | 8149 |  |  | 8148 |  |  | -1972 | -1972 | -1971 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 414
20250525 | May | 1330 | 8149 |  |  | 8148 |  |  | -1972 | -1972 | -1971 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 1430 | 8149 |  |  | 8148 |  |  | -1972 | -1972 | -1971 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 1530 | 8620 |  |  | 8594 |  |  | -3090 | -3090 | -3065 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250525 | May | 1630 | 8620 |  |  | 8594 |  |  | -3090 | -3090 | -3065 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 336
20250525 | May | 1730 | 8620 |  |  | 8224 |  |  | -3090 | -3090 | -2695 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 336
20250525 | May | 1830 |  | 6281 | 566 |  | 6281 | 566 | -661 | -661 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1264 | NA | -5149 |  |  | AT | 336
20250525 | May | 1930 |  | 6281 | 566 |  | 6281 | 566 | -661 | -661 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1364 | NA | -5149 |  |  | AT | 328
20250525 | May | 2030 |  | 6281 | 566 |  | 6281 | 566 | -661 | -661 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1464 | NA | -5149 |  |  | AT | 328
20250525 | May | 2130 |  | 6156 | 554 |  | 6155 | 554 | -164 | -164 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1576 | NA | -5047 |  |  | AT | 330
20250526 | May | 1230 | 5789 |  |  | 5783 |  |  | 2449 | 159 | 2296 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5533 | Reduction due to missing redispatch potential
20250526 | May | 1330 | 5789 |  |  | 5783 |  |  | 2449 | 159 | 2296 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5533 | Reduction due to missing redispatch potential | FR | 2701 | Process fail during TSO validation phase
20250526 | May | 1430 | 5799 |  |  | 5793 |  |  | 2449 | 169 | 2286 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5543 | Reduction due to missing redispatch potential | FR | 2701 | Process fail during TSO validation phase
20250526 | May | 1530 |  | 5370 | 340 |  | 5283 | 340 | 728 | 152 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1190 | NA | -4603 | [8 empty] | FR | 2701 | Process fail during TSO validation phase
20250526 | May | 1830 | 5984 |  |  | 5973 |  |  | 1780 | 204 | 1587 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5723 | Reduction due to missing redispatch potential
20250526 | May | 2030 | 5832 |  |  | 5829 |  |  | 1780 | 52 | 1731 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5579 | Reduction due to missing redispatch potential
20250526 | May | 2230 |  | 5532 | 444 |  | 5532 | 444 | 2513 | 167 | 0 | Minimum Margin | Minimum Margin | 1786 | NA | -4644 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250526 | May | 2330 |  | 5191 | 471 |  | 5190 | 471 | 2875 | 185 | 0 | Minimum Margin | Minimum Margin | 1859 | NA | -4248 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250527 | May | 30 | 7581 |  |  | 7579 |  |  | 1426 | 139 | 1288 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250527 | May | 130 | 7778 |  |  | 7631 |  |  | 1426 | 336 | 1235 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250527 | May | 230 | 7630 |  |  | 7625 |  |  | 1426 | 188 | 1241 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250527 | May | 330 | 8057 |  |  | 8027 |  |  | -1992 | -1992 | -1961 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250527 | May | 430 | 8057 |  |  | 8027 |  |  | -1992 | -1992 | -1961 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250527 | May | 530 | 8057 |  |  | 8027 |  |  | -1992 | -1992 | -1961 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 416
20250527 | May | 630 | 7857 |  |  | 7826 |  |  | -1764 | -1764 | -1731 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 416
20250527 | May | 730 | 7646 |  |  | 7509 |  |  | 1046 | 0 | 1183 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250527 | May | 830 | 7647 |  |  | 7509 |  |  | 1046 | 1 | 1183 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250527 | May | 930 | 8566 |  |  | 8016 |  |  | -1489 | -1489 | -937 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250527 | May | 1030 | 8566 |  |  | 8016 |  |  | -1489 | -1489 | -937 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 422
20250527 | May | 1130 | 8566 |  |  | 8016 |  |  | -1489 | -1489 | -937 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 422
20250527 | May | 1230 | 7757 |  |  | 7757 |  |  | -1659 | -1659 | -1658 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 422
20250527 | May | 1330 | 7757 |  |  | 7757 |  |  | -1659 | -1659 | -1658 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 364
20250527 | May | 1430 | 7757 |  |  | 7757 |  |  | -1659 | -1659 | -1658 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 364
20250527 | May | 1530 | 6759 |  |  | 6759 |  |  | 1722 | 2 | 1720 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 370
20250527 | May | 1630 | 6759 |  |  | 6759 |  |  | 1722 | 2 | 1720 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 411
20250527 | May | 1730 | 6870 |  |  | 6863 |  |  | 1722 | 113 | 1615 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 411
20250527 | May | 1830 |  | 7166 | 642 |  | 7165 | 642 | -734 | -734 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1188 | NA | -5881 |  |  | AT | 411
20250527 | May | 1930 |  | 7166 | 642 |  | 7165 | 642 | -734 | -734 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1288 | NA | -5881 |  |  | AT | 381
20250527 | May | 2030 |  | 7166 | 642 |  | 7165 | 642 | -734 | -734 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1388 | NA | -5881 |  |  | AT | 375
20250527 | May | 2130 |  | 6667 | 597 |  | 6667 | 597 | 984 | 126 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1533 | NA | -5473 |  |  | AT | 362
20250528 | May | 2230 | 6385 |  |  | 6385 |  |  | -2531 | -2531 | -2531 | Critical Branch | Critical Branch | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250528 | May | 2330 | 5985 |  |  | 5985 |  |  | -2126 | -2126 | -2126 | Critical Branch | Critical Branch | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 30 | 8165 |  |  | 7316 |  |  | -2243 | -2243 | -1394 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 130 | 8165 |  |  | 7316 |  |  | -2243 | -2243 | -1394 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 230 | 8165 |  |  | 7316 |  |  | -2243 | -2243 | -1394 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 330 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 430 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 530 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425
20250529 | May | 630 | 8410 |  |  | 7825 |  |  | -1950 | -1950 | -1364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425
20250529 | May | 730 | 7950 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421
20250529 | May | 830 | 7950 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421
20250529 | May | 930 | 7897 |  |  | 6552 |  |  | -1973 | -1973 | -628 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 421
20250529 | May | 1030 | 7897 |  |  | 6552 |  |  | -1973 | -1973 | -628 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 375
20250529 | May | 1130 | 7897 |  |  | 6552 |  |  | -1973 | -1973 | -628 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 375
20250529 | May | 1230 | 7078 |  |  | 6145 |  |  | -1297 | -1297 | -364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 375
20250529 | May | 1330 | 7078 |  |  | 6145 |  |  | -1297 | -1297 | -364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 327
20250529 | May | 1430 | 7078 |  |  | 6145 |  |  | -1297 | -1297 | -364 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 331
20250529 | May | 1530 |  | 5791 | 523 |  | 5791 | 523 | -735 | -735 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1007 | NA | -4745 |  |  | AT | 331
20250529 | May | 1630 |  | 6091 | 523 |  | 6091 | 523 | -1057 | -1057 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1107 | NA | -5045 |  |  | AT | 312
20250529 | May | 1730 |  | 6091 | 523 |  | 6091 | 523 | -1057 | -1057 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1207 | NA | -5045 |  |  | AT | 312
20250529 | May | 1830 |  | 5778 | 496 |  | 5777 | 496 | -2205 | -2205 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1334 | NA | -4785 |  |  | AT | 312
20250529 | May | 1930 |  | 5778 | 496 |  | 5777 | 496 | -2205 | -2205 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1434 | NA | -4785 |  |  | AT | 308
20250529 | May | 2030 |  | 5778 | 496 |  | 5777 | 496 | -2205 | -2205 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1534 | NA | -4785 |  |  | AT | 308
20250529 | May | 2130 | 6129 |  |  | 6128 |  |  | -1623 | -1623 | -1623 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 295
20250529 | May | 2230 | 6129 |  |  | 6128 |  |  | -1623 | -1623 | -1623 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250529 | May | 2330 | 5729 |  |  | 5729 |  |  | -1225 | -1225 | -1225 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250530 | May | 30 | 8621 |  |  | 8467 |  |  | -1374 | -1374 | -1233 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250530 | May | 130 | 8621 |  |  | 8467 |  |  | -1374 | -1374 | -1233 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 359 | Reduction because NTC over thermal limit on border
20250530 | May | 230 | 8621 |  |  | 8467 |  |  | -1374 | -1374 | -1233 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250530 | May | 330 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250530 | May | 430 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250530 | May | 530 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 407 | Reduction because NTC over thermal limit on border
20250530 | May | 630 | 8558 |  |  | 8433 |  |  | -1892 | -1892 | -1778 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 379 | Reduction because NTC over thermal limit on border
20250530 | May | 730 | 7925 |  |  | 7925 |  |  | -206 | -206 | -206 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 310 | Reduction because NTC over thermal limit on border
20250530 | May | 830 | 7925 |  |  | 7661 |  |  | -206 | -206 | 52 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 255 | Reduction because NTC over thermal limit on border
20250530 | May | 930 | 6167 |  |  | 6161 |  |  | 2131 | 87 | 2051 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 315 | Reduction because NTC over thermal limit on border
20250530 | May | 1030 | 6297 |  |  | 6250 |  |  | 2131 | 217 | 1961 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 313 | Reduction because NTC over thermal limit on border
20250530 | May | 1130 | 6293 |  |  | 6250 |  |  | 2131 | 213 | 1961 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 315 | Reduction because NTC over thermal limit on border
20250530 | May | 1230 | 6232 |  |  | 6221 |  |  | 2621 | 152 | 2480 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 314 | Reduction because NTC over thermal limit on border
20250530 | May | 1330 | 6263 |  |  | 6249 |  |  | 2621 | 183 | 2452 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 316 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2767 | Process fail during TSO validation phase
20250530 | May | 1430 | 6246 |  |  | 6234 |  |  | 2621 | 166 | 2467 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 313 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2767 | Process fail during TSO validation phase
20250530 | May | 1530 |  | 5835 | 387 |  | 5741 | 387 | 1967 | 174 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1143 | NA | -4967 |  |  | AT | 315 | Reduction because NTC over thermal limit on border |  |  |  | FR | 2767 | Process fail during TSO validation phase
20250530 | May | 1630 |  | 5790 | 383 |  | 5720 | 383 | 1967 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1247 | NA | -4954 |  |  | AT | 104 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3329 | Process fail during TSO validation phase
20250530 | May | 1730 |  | 5830 | 386 |  | 5738 | 386 | 1967 | 169 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1344 | NA | -4966 |  |  | AT | 379 |  |  |  |  | FR | 3329 | Process fail during TSO validation phase
20250530 | May | 1830 |  | 6753 | 580 |  | 6732 | 580 | 2195 | 37 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1250 | NA | -5572 |  |  | AT | 379 |  |  |  |  | FR | 3329 | Process fail during TSO validation phase
20250530 | May | 1930 |  | 6909 | 594 |  | 6805 | 594 | 2195 | 193 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1336 | NA | -5617 |  |  | AT | 368
20250530 | May | 2030 |  | 6901 | 593 |  | 6802 | 593 | 2195 | 185 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1437 | NA | -5616 |  |  | AT | 368
20250530 | May | 2130 | 7214 |  |  | 7214 |  |  | -1554 | -1554 | -1554 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 356
20250530 | May | 2230 | 7214 |  |  | 7214 |  |  | -1554 | -1554 | -1554 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 328
20250530 | May | 2330 | 6814 |  |  | 6813 |  |  | -1157 | -1157 | -1157 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 328
20250531 | May | 30 | 6313 |  |  | 6313 |  |  | -703 | -703 | -703 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 328
20250531 | May | 130 | 6313 |  |  | 6313 |  |  | -703 | -703 | -703 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 317
20250531 | May | 230 | 6313 |  |  | 6313 |  |  | -703 | -703 | -703 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 319
20250531 | May | 330 | 6129 |  |  | 6128 |  |  | 26 | 0 | 27 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 319
20250531 | May | 430 | 6155 |  |  | 6155 |  |  | 26 | 26 | 0 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 317
20250531 | May | 530 | 6155 |  |  | 6155 |  |  | 26 | 26 | 0 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 310
20250531 | May | 630 | 6130 |  |  | 6129 |  |  | 26 | 1 | 26 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 310
20250531 | May | 730 | 6154 |  |  | 6154 |  |  | -333 | -333 | -333 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 392
20250531 | May | 830 | 6154 |  |  | 6154 |  |  | -333 | -333 | -333 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250531 | May | 930 | 8306 |  |  | 7654 |  |  | -1848 | -1848 | -1197 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250531 | May | 1030 | 8306 |  |  | 8229 |  |  | -1848 | -1848 | -1771 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 369
20250531 | May | 1130 | 8306 |  |  | 8229 |  |  | -1848 | -1848 | -1771 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 369
20250531 | May | 1230 | 7230 |  |  | 7230 |  |  | -1287 | -1287 | -1287 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 369
20250531 | May | 1330 | 7230 |  |  | 7230 |  |  | -1287 | -1287 | -1287 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 328
20250531 | May | 1430 | 7230 |  |  | 7230 |  |  | -1287 | -1287 | -1287 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 328
20250531 | May | 1530 | 6483 |  |  | 6483 |  |  | -694 | -694 | -694 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 328
20250531 | May | 1630 | 6483 |  |  | 6483 |  |  | -694 | -694 | -694 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 353 |  |  |  |  | FR | 3196 | Process fail during TSO validation phase
20250531 | May | 1730 | 6483 |  |  | 6483 |  |  | -694 | -694 | -694 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 353 |  |  |  |  | FR | 3196 | Process fail during TSO validation phase
20250531 | May | 1830 |  | 6468 | 555 |  | 6466 | 555 | 2276 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1275 | NA | -5356 |  |  | AT | 353 |  |  |  |  | FR | 3196 | Process fail during TSO validation phase
20250531 | May | 1930 |  | 6468 | 555 |  | 6466 | 555 | 2276 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1375 | NA | -5356 |  |  | AT | 306
20250531 | May | 2030 |  | 6468 | 555 |  | 6466 | 555 | 2276 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1475 | NA | -5356 |  |  | AT | 306
20250531 | May | 2130 | 6080 |  |  | 6080 |  |  | -1278 | -1278 | -1278 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 292
20250531 | May | 2230 | 6080 |  |  | 6080 |  |  | -1278 | -1278 | -1278 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250531 | May | 2330 | 5680 |  |  | 5680 |  |  | -883 | -883 | -883 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 30 | 8165 |  |  | 8147 |  |  | -1440 | -1440 | -1429 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 130 | 8165 |  |  | 8147 |  |  | -1440 | -1440 | -1429 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 230 | 8165 |  |  | 8147 |  |  | -1440 | -1440 | -1429 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 330 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -556 | NA | -6761 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 430 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -456 | NA | -6761 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 530 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -356 | NA | -6761 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 630 |  | 8611 | 886 |  | 8533 | 886 | -2444 | -2444 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -256 | NA | -6761 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 730 |  | 7564 | 975 |  | 7564 | 954 | 385 | 323 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -245 | NA | -5656 |  |  | AT | 343
20250601 | June | 830 |  | 7613 | 981 |  | 7034 | 959 | 385 | 372 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -151 | NA | -5116 |  |  | AT | 343
20250601 | June | 930 | 6495 |  |  | 6495 |  |  | -319 | -319 | -319 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 343
20250601 | June | 1030 | 6495 |  |  | 6495 |  |  | -319 | -319 | -319 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 392
20250601 | June | 1130 | 6495 |  |  | 6495 |  |  | -319 | -319 | -319 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 392
20250601 | June | 1230 | 7340 |  |  | 7340 |  |  | -801 | -801 | -801 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 392
20250601 | June | 1330 | 7340 |  |  | 7340 |  |  | -801 | -801 | -801 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 370
20250601 | June | 1430 | 7340 |  |  | 7340 |  |  | -801 | -801 | -801 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 370
20250601 | June | 1530 | 6965 |  |  | 6964 |  |  | -520 | -520 | -520 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 370
20250601 | June | 1630 | 6965 |  |  | 6964 |  |  | -520 | -520 | -520 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 1730 | 6965 |  |  | 6964 |  |  | -520 | -520 | -520 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 1830 |  | 7588 | 735 |  | 7564 | 735 | -322 | -322 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1095 | NA | -6094 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 1930 |  | 7588 | 735 |  | 7564 | 735 | -322 | -322 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1195 | NA | -6094 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 2030 |  | 7588 | 735 |  | 7564 | 735 | -322 | -322 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1295 | NA | -6094 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 2130 |  | 7931 | 778 |  | 7885 | 778 | -2590 | -2590 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1352 | NA | -6329 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250601 | June | 2230 |  | 7931 | 778 |  | 7885 | 778 | -2590 | -2590 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1452 | NA | -6329 |  |  | AT | 231 | Reduction because NTC over thermal limit on border |  |  |  | FR | 4325 | Process fail during TSO validation phase
20250601 | June | 2330 |  | 8138 | 778 |  | 8088 | 778 | -2704 | -2704 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1552 | NA | -6532 |  |  | AT | 231 | Reduction because NTC over thermal limit on border |  |  |  | FR | 4325 | Process fail during TSO validation phase
20250602 | June | 30 |  | 8205 | 1031 |  | 8168 | 998 | 395 | 64 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -1001 | NA | -6172 |  |  | AT | 231 | Reduction because NTC over thermal limit on border |  |  |  | FR | 4325 | Process fail during TSO validation phase
20250602 | June | 130 |  | 8205 | 1031 |  | 8168 | 998 | 395 | 64 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -901 | NA | -6172 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250602 | June | 230 |  | 8205 | 1031 |  | 8168 | 998 | 395 | 64 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | -801 | NA | -6172 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250602 | June | 330 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -367 | NA | -6018 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250602 | June | 430 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -267 | NA | -6018 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250602 | June | 530 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -167 | NA | -6018 |  |  | AT | 193 | Reduction because NTC over thermal limit on border
20250602 | June | 630 |  | 7418 | 697 |  | 7412 | 697 | 1232 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -67 | NA | -6018 |  |  | AT | 192 | Reduction because NTC over thermal limit on border
20250602 | June | 730 |  | 6882 | 883 |  | 6882 | 880 | -2915 | -2915 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -153 | NA | -5122 |  |  | AT | 298 | Reduction because NTC over thermal limit on border
20250602 | June | 830 |  | 6882 | 883 |  | 6821 | 880 | -2915 | -2915 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -53 | NA | -5061 |  |  | AT | 298 | Reduction because NTC over thermal limit on border
20250602 | June | 930 | 5815 |  |  | 5804 |  |  | 4529 | 135 | 4405 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 299 | Reduction because NTC over thermal limit on border
20250602 | June | 1030 | 5815 |  |  | 5804 |  |  | 4529 | 135 | 4405 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 385 | Reduction because NTC over thermal limit on border
20250602 | June | 1130 | 5823 |  |  | 5811 |  |  | 4529 | 143 | 4398 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 414 | Reduction because NTC over thermal limit on border
20250602 | June | 1230 | 7845 |  |  | 7311 |  |  | -1800 | -1800 | -1280 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 377 | Reduction because NTC over thermal limit on border
20250602 | June | 1330 | 7845 |  |  | 7844 |  |  | -1800 | -1800 | -1799 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 291 | Reduction because NTC over thermal limit on border
20250602 | June | 1430 | 7845 |  |  | 7180 |  |  | -1800 | -1800 | -1152 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 291 | Reduction because NTC over thermal limit on border
20250602 | June | 1530 | 5680 |  |  | 5680 |  |  | -1382 | -1382 | -1382 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 291 | Reduction because NTC over thermal limit on border
20250602 | June | 1630 | 5680 |  |  | 5680 |  |  | -1382 | -1382 | -1382 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 379 | Reduction because NTC over thermal limit on border
20250602 | June | 1730 | 5680 |  |  | 5680 |  |  | -1382 | -1382 | -1382 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 382 | Reduction because NTC over thermal limit on border
20250602 | June | 1830 |  | 6793 | 639 |  | 6741 | 639 | 3875 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1191 | NA | -5463 |  |  | AT | 382 | Reduction because NTC over thermal limit on border
20250602 | June | 1930 |  | 6793 | 639 |  | 6792 | 639 | 3875 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1291 | NA | -5514 |  |  | AT | 366
20250602 | June | 2030 |  | 6793 | 639 |  | 6792 | 639 | 3875 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1391 | NA | -5514 |  |  | AT | 366
20250602 | June | 2130 |  | 4979 | 609 |  | 4979 | 608 | -2179 | -2179 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1521 | NA | -3763 |  |  | AT | 367
20250603 | June | 1030 | 6585 |  |  | 6582 |  |  | 2421 | 130 | 2294 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6332 | Reduction due to missing redispatch potential
20250603 | June | 1130 | 6654 |  |  | 6651 |  |  | 2421 | 199 | 2225 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6401 | Reduction due to missing redispatch potential
20250603 | June | 1230 | 7145 |  |  | 7139 |  |  | 2804 | 170 | 2640 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6889 | Reduction due to missing redispatch potential
20250603 | June | 1330 | 7145 |  |  | 7139 |  |  | 2804 | 170 | 2640 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6889 | Reduction due to missing redispatch potential
20250603 | June | 1430 | 7145 |  |  | 7139 |  |  | 2804 | 170 | 2640 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6889 | Reduction due to missing redispatch potential
20250603 | June | 1530 | 6541 |  |  | 6539 |  |  | 2258 | 189 | 2071 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6289 | Reduction due to missing redispatch potential
20250603 | June | 1630 | 6554 |  |  | 6548 |  |  | 2258 | 202 | 2062 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6302 | Reduction due to missing redispatch potential
20250604 | June | 530 | 6760 |  |  | 6760 |  |  | -1112 | -1112 | -1112 | Critical Branch | Critical Branch | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 630 | 6560 |  |  | 6485 |  |  | -891 | -891 | -817 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | [6 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 730 | 5617 |  |  | 4985 |  |  | -1119 | -1119 | -493 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 830 | 5617 |  |  | 4985 |  |  | -1119 | -1119 | -493 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 930 | 5232 |  |  | 4776 |  |  | 3701 | 2 | 4660 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1030 | 5463 |  |  | 4895 |  |  | 3701 | 233 | 4652 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 5201 | Reduction due to missing redispatch potential | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1130 | 5232 |  |  | 4776 |  |  | 3701 | 2 | 4660 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1230 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1330 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1430 | 7400 |  |  | 5956 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250604 | June | 1730 | 8100 |  |  | 7456 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250604 | June | 2230 |  | 5661 | 389 |  | 5661 | 389 | -3204 | -3204 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 1841 | NA | -4883 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3931 | Cancellation planned outage Chaffard G.Ile 2
20250604 | June | 2330 |  | 5301 | 414 |  | 5301 | 414 | -2807 | -2807 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 1916 | NA | -4473 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3931 | Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 30 | 8739 |  |  | 6300 |  |  | -3107 | -3107 | -915 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3931 | Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 130 | 8739 |  |  | 6300 |  |  | -3107 | -3107 | -915 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3822 | Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 230 | 8739 |  |  | 6300 |  |  | -3107 | -3107 | -915 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3822 | Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 330 | 8517 |  |  | 6223 |  |  | -2580 | -2580 | -531 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3822 | Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 430 | 8517 |  |  | 6223 |  |  | -2580 | -2580 | -531 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3822 | Cancellation planned outage Chaffard G.Ile 2
20250605 | June | 530 | 8517 |  |  | 6223 |  |  | -2580 | -2580 | -531 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 397 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 630 | 8317 |  |  | 6013 |  |  | -2353 | -2353 | -285 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 384 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 730 | 6960 |  |  | 5716 |  |  | 5101 | 19 | 7663 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 292 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 830 | 6958 |  |  | 5702 |  |  | 5101 | 17 | 7667 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 305 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 930 | 5245 |  |  | 4783 |  |  | 4149 | 15 | 5103 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 304 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1030 | 5452 |  |  | 4892 |  |  | 4149 | 222 | 5094 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 304 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1130 | 5438 |  |  | 4884 |  |  | 4149 | 208 | 5095 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 304 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1230 | 5437 |  |  | 4885 |  |  | 3669 | 207 | 4615 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 304 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1330 | 5437 |  |  | 4885 |  |  | 3669 | 207 | 4615 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 291 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1430 | 5439 |  |  | 4886 |  |  | 3669 | 209 | 4615 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 291 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1530 | 5234 |  |  | 4776 |  |  | 3776 | 4 | 4730 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 304 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250605 | June | 1630 | 5241 |  |  | 4780 |  |  | 3776 | 11 | 4729 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 334
20250605 | June | 1730 | 5942 |  |  | 4889 |  |  | 2297 | 12 | 4288 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 334
20250605 | June | 1830 |  | 6153 | 528 |  | 5924 | 528 | -2650 | -2650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1302 | NA | -4868 |  |  | AT | 334
20250605 | June | 1930 |  | 6153 | 528 |  | 6152 | 528 | -2650 | -2650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1402 | NA | -5096 |  |  | AT | 355
20250605 | June | 2030 |  | 6153 | 528 |  | 6152 | 528 | -2650 | -2650 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1502 | NA | -5096 |  |  | AT | 355
20250605 | June | 2130 | 6983 |  |  | 6982 |  |  | -2595 | -2595 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 343
20250605 | June | 2230 | 6983 |  |  | 6982 |  |  | -2595 | -2595 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250605 | June | 2330 | 6583 |  |  | 6583 |  |  | -2198 | -2198 | -2198 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 30 | 9213 |  |  | 8690 |  |  | -3262 | -3262 | -2736 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 130 | 9213 |  |  | 8690 |  |  | -3262 | -3262 | -2736 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 230 | 9213 |  |  | 8690 |  |  | -3262 | -3262 | -2736 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 330 | 8997 |  |  | 8690 |  |  | -1597 | -1597 | -1311 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 430 | 8997 |  |  | 8690 |  |  | -1597 | -1597 | -1311 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 530 | 8997 |  |  | 8544 |  |  | -1597 | -1597 | -1165 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 378 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 630 | 8797 |  |  | 7044 |  |  | -1467 | -1467 | 265 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 378 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 730 | 7267 |  |  | 5544 |  |  | 2266 | 0 | 5524 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 304 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 830 | 7267 |  |  | 5544 |  |  | 2266 | 0 | 5524 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 307 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 930 | 5953 |  |  | 4894 |  |  | 3218 | 23 | 5211 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 303 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1030 | 6002 |  |  | 4918 |  |  | 3218 | 72 | 5209 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 351 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1130 | 5930 |  |  | 4883 |  |  | 3218 | 0 | 5212 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 351 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1230 | 6779 |  |  | 5303 |  |  | -3754 | -3754 | -2351 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 351 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1330 | 6779 |  |  | 5303 |  |  | -3754 | -3754 | -2351 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1430 | 6779 |  |  | 5303 |  |  | -3754 | -3754 | -2351 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1530 | 7503 |  |  | 5660 |  |  | -4302 | -4302 | -2553 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391 |  |  |  |  | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
20250606 | June | 1630 | 7503 |  |  | 5660 |  |  | -4302 | -4302 | -2553 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 337
20250606 | June | 1730 | 7503 |  |  | 5660 |  |  | -4302 | -4302 | -2553 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 338
20250606 | June | 1830 |  | 6202 | 532 |  | 6201 | 532 | 4574 | 111 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1298 | NA | -5137 |  |  | AT | 331
20250606 | June | 1930 |  | 6205 | 533 |  | 6205 | 533 | 4574 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1397 | NA | -5139 |  |  | AT | 413
20250606 | June | 2030 |  | 6093 | 523 |  | 6093 | 523 | 4574 | 2 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1507 | NA | -5047 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250606 | June | 2130 |  | 7841 | 673 |  | 7480 | 673 | -1814 | -1814 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1457 | NA | -6134 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250606 | June | 2230 |  | 7841 | 673 |  | 7832 | 673 | -1814 | -1814 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1557 | NA | -6486 |  |  | AT | 361
20250606 | June | 2330 |  | 7481 | 698 |  | 7471 | 698 | -1391 | -1391 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1632 | NA | -6075 |  |  | AT | 361
20250607 | June | 30 | 6904 |  |  | 6903 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 361
20250607 | June | 130 | 6904 |  |  | 6903 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 405
20250607 | June | 230 | 6904 |  |  | 6903 |  |  | -2091 | -2091 | -2091 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 405
20250607 | June | 330 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -344 | NA | -5819 |  |  | AT | 405
20250607 | June | 430 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -244 | NA | -5819 |  |  | AT | 405
20250607 | June | 530 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -144 | NA | -5819 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 630 |  | 7168 | 674 |  | 7167 | 674 | -2446 | -2446 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -44 | NA | -5819 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 730 | 8744 |  |  | 8551 |  |  | -2498 | -2498 | -2308 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425
20250607 | June | 830 | 8744 |  |  | 8551 |  |  | -2498 | -2498 | -2308 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425
20250607 | June | 930 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425
20250607 | June | 1030 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250607 | June | 1130 | 8250 |  |  | 8250 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250607 | June | 1230 | 7530 |  |  | 7529 |  |  | -3991 | -3991 | -3990 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250607 | June | 1330 | 7530 |  |  | 7529 |  |  | -3991 | -3991 | -3990 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 1430 | 7530 |  |  | 7529 |  |  | -3991 | -3991 | -3990 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 1530 | 8496 |  |  | 8483 |  |  | -3331 | -3331 | -3318 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 1630 | 8496 |  |  | 8483 |  |  | -3331 | -3331 | -3318 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 1730 | 8496 |  |  | 8483 |  |  | -3331 | -3331 | -3318 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 1830 | 8547 |  |  | 8531 |  |  | -1914 | -1914 | -1904 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250607 | June | 1930 | 8547 |  |  | 8531 |  |  | -1914 | -1914 | -1904 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250607 | June | 2030 | 8547 |  |  | 8531 |  |  | -1914 | -1914 | -1904 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250607 | June | 2130 | 8076 |  |  | 8076 |  |  | -2140 | -2140 | -2140 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 405
20250607 | June | 2230 | 8076 |  |  | 8076 |  |  | -2140 | -2140 | -2140 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250607 | June | 2330 | 7676 |  |  | 7676 |  |  | -1743 | -1743 | -1743 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250608 | June | 30 | 8604 |  |  | 8561 |  |  | -1985 | -1985 | -1946 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250608 | June | 130 | 8604 |  |  | 8561 |  |  | -1985 | -1985 | -1946 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 230 | 8604 |  |  | 8561 |  |  | -1985 | -1985 | -1946 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 430 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 530 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 630 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 730 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 830 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 930 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 1030 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 1130 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250608 | June | 1230 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 385
20250608 | June | 1330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 291
20250608 | June | 1430 | 7850 |  |  | 7319 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 291
20250608 | June | 1530 |  | 5298 | 451 |  | 5298 | 451 | -2876 | -2876 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1079 | NA | -4396 |  |  | AT | 291
20250608 | June | 1630 |  | 5298 | 451 |  | 5298 | 451 | -2876 | -2876 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1179 | NA | -4396 |  |  | AT | 385 |  |  |  |  | FR | 3437 | Process fail during TSO validation phase
20250608 | June | 1730 |  | 5298 | 451 |  | 5298 | 451 | -2876 | -2876 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1279 | NA | -4396 |  |  | AT | 394
20250608 | June | 1830 |  | 7110 | 668 |  | 6826 | 668 | 877 | 129 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1162 | NA | -5490 |  |  | AT | 394
20250608 | June | 1930 |  | 6981 | 656 |  | 6981 | 656 | 877 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1274 | NA | -5669 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250608 | June | 2030 |  | 6981 | 656 |  | 6981 | 656 | 877 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1374 | NA | -5669 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250608 | June | 2130 |  | 8209 | 780 |  | 8155 | 780 | -2724 | -2724 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1350 | NA | -6595 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250608 | June | 2230 |  | 8209 | 780 |  | 8155 | 780 | -2724 | -2724 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1450 | NA | -6595 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250608 | June | 2330 |  | 8209 | 780 |  | 8155 | 780 | -2724 | -2724 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1550 | NA | -6595 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250609 | June | 30 | 8031 |  |  | 8021 |  |  | -2071 | -2071 | -2060 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250609 | June | 130 | 8031 |  |  | 8021 |  |  | -2071 | -2071 | -2060 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250609 | June | 230 | 8031 |  |  | 8021 |  |  | -2071 | -2071 | -2060 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250609 | June | 330 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -526 | NA | -5894 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250609 | June | 430 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -426 | NA | -5894 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250609 | June | 530 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -326 | NA | -5894 |  |  | AT | 339
20250609 | June | 630 |  | 7624 | 856 |  | 7606 | 856 | -1503 | -1503 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | -226 | NA | -5894 |  |  | AT | 339
20250609 | June | 730 |  | 6225 | 539 |  | 6225 | 539 | -822 | -822 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 191 | NA | -5147 |  |  | AT | 409
20250609 | June | 830 |  | 6225 | 539 |  | 6225 | 539 | -822 | -822 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 291 | NA | -5147 |  |  | AT | 410
20250609 | June | 930 | 7993 |  |  | 7965 |  |  | -5511 | -5511 | -5483 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 404
20250609 | June | 1030 | 7993 |  |  | 7992 |  |  | -5511 | -5511 | -5510 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 333
20250609 | June | 1130 | 7993 |  |  | 7867 |  |  | -5511 | -5511 | -5385 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 333
20250609 | June | 1230 |  | 6131 | 695 |  | 6130 | 695 | -195 | -195 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 535 | NA | -4740 |  |  | AT | 333
20250609 | June | 1330 |  | 6131 | 695 |  | 6130 | 695 | -195 | -195 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 635 | NA | -4740 |  |  | AT | 415
20250609 | June | 1430 |  | 6131 | 695 |  | 6130 | 695 | -195 | -195 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 735 | NA | -4740 |  |  | AT | 415
20250609 | June | 1530 |  | 7518 | 722 |  | 7518 | 722 | -1773 | -1773 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 808 | NA | -6074 |  |  | AT | 402
20250609 | June | 1630 |  | 7518 | 722 |  | 7518 | 722 | -1773 | -1773 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 908 | NA | -6074 |  |  | AT | 305
20250609 | June | 1730 |  | 7518 | 722 |  | 7300 | 722 | -1773 | -1773 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1008 | NA | -5856 |  |  | AT | 305
20250609 | June | 1830 |  | 5661 | 399 |  | 5660 | 399 | -2258 | -2258 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1431 | NA | -4862 |  |  | AT | 305
20250609 | June | 1930 |  | 5661 | 399 |  | 5660 | 399 | -2258 | -2258 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1531 | NA | -4862 |  |  | AT | 305
20250609 | June | 2030 |  | 5661 | 399 |  | 5660 | 399 | -2258 | -2258 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1631 | NA | -4862 |  |  | AT | 305
20250609 | June | 2130 |  | 5661 | 453 |  | 5660 | 453 | -2252 | -2252 | 0 | TTC Selection - LTTCImport | TTC Validation phase - bilateral reduction | 1677 | NA | -4754 |  |  | AT | 292
20250610 | June | 1530 | 7041 |  |  | 7035 |  |  | 2759 | 102 | 2663 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6785 | Reduction due to missing redispatch potential
20250610 | June | 1630 | 7109 |  |  | 7098 |  |  | 2759 | 170 | 2600 | Minimum Margin | Validation phase | NA | NA | 0 | [5 empty] | CH | 6848 | Reduction due to missing redispatch potential
20250610 | June | 1730 | 7103 |  |  | 6680 |  |  | 2759 | 164 | 3018 | Minimum Margin | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp |  |  |  | CH | 6843 | Reduction due to missing redispatch potential
20250610 | June | 2230 |  | 4776 | 411 |  | 4776 | 411 | -1311 | -1311 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 1819 | NA | -3954 |  |  | AT | 376
20250610 | June | 2330 |  | 4416 | 436 |  | 4416 | 436 | -911 | -911 | 0 | TTC Selection - LTTCImport | TTC Selection - LTTCImport | 1894 | NA | -3544 |  |  | AT | 376
20250611 | June | 30 | 6353 |  |  | 6352 |  |  | -2074 | -2074 | -2073 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 376
20250611 | June | 130 | 6353 |  |  | 6352 |  |  | -2074 | -2074 | -2073 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250611 | June | 230 | 6353 |  |  | 6352 |  |  | -2074 | -2074 | -2073 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250611 | June | 330 | 6591 |  |  | 6590 |  |  | -1134 | -1134 | -1134 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250611 | June | 430 | 6591 |  |  | 6590 |  |  | -1134 | -1134 | -1134 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250611 | June | 530 | 6591 |  |  | 6590 |  |  | -1134 | -1134 | -1134 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 347
20250611 | June | 630 | 6391 |  |  | 6391 |  |  | -938 | -938 | -937 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 347
20250611 | June | 730 | 5237 |  |  | 5237 |  |  | -1713 | -1713 | -1713 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 381
20250611 | June | 830 | 5237 |  |  | 5237 |  |  | -1713 | -1713 | -1713 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 375
20250611 | June | 930 | 5713 |  |  | 5710 |  |  | 4243 | 89 | 4156 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 375
20250611 | June | 1030 | 5624 |  |  | 5624 |  |  | 4243 | 0 | 4243 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 399
20250611 | June | 1130 | 5624 |  |  | 5624 |  |  | 4243 | 0 | 4243 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 399
20250611 | June | 1230 | 5958 |  |  | 5957 |  |  | -3307 | -3307 | -3305 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 399
20250611 | June | 1330 | 5958 |  |  | 5957 |  |  | -3307 | -3307 | -3305 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 1430 | 5958 |  |  | 5957 |  |  | -3307 | -3307 | -3305 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 1530 | 6380 |  |  | 6374 |  |  | -3651 | -3651 | -3643 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 1630 | 6380 |  |  | 6374 |  |  | -3651 | -3651 | -3643 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 1730 | 7280 |  |  | 7275 |  |  | -4570 | -4570 | -4564 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 1830 |  | 8048 | 834 |  | 7962 | 834 | -2538 | -2538 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 996 | NA | -6294 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 1930 |  | 8048 | 834 |  | 7962 | 834 | -2538 | -2538 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1096 | NA | -6294 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 2030 |  | 8048 | 834 |  | 7962 | 834 | -2538 | -2538 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1196 | NA | -6294 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250611 | June | 2130 |  | 7766 | 783 |  | 7699 | 783 | 471 | 107 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1347 | NA | -6133 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250611 | June | 2230 |  | 7665 | 774 |  | 7605 | 774 | 471 | 6 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1456 | NA | -6057 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250611 | June | 2330 |  | 7394 | 809 |  | 7326 | 809 | 882 | 114 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1521 | NA | -5708 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 30 | 8270 |  |  | 6950 |  |  | -4919 | -4919 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 130 | 8270 |  |  | 6950 |  |  | -4919 | -4919 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 230 | 8270 |  |  | 6950 |  |  | -4919 | -4919 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 330 | 7955 |  |  | 6950 |  |  | -4528 | -4528 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 430 | 7955 |  |  | 6950 |  |  | -4528 | -4528 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 530 | 7955 |  |  | 6950 |  |  | -4528 | -4528 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 630 | 7755 |  |  | 6750 |  |  | -4318 | -4318 | 0 | Critical Branch | Scheduled TTC | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 730 | 7854 |  |  | 7200 |  |  | -4602 | -4602 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 354
20250612 | June | 830 | 7854 |  |  | 7200 |  |  | -4602 | -4602 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 354
20250612 | June | 930 | 6094 |  |  | 6093 |  |  | -2913 | -2913 | -2912 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 354
20250612 | June | 1030 | 6094 |  |  | 6093 |  |  | -2913 | -2913 | -2912 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 1130 | 6094 |  |  | 6093 |  |  | -2913 | -2913 | -2912 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 1230 | 7365 |  |  | 7200 |  |  | -1017 | -1017 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 1330 | 7365 |  |  | 7200 |  |  | -1017 | -1017 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 397
20250612 | June | 1430 | 7365 |  |  | 7200 |  |  | -1017 | -1017 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 397
20250612 | June | 1530 | 6761 |  |  | 6761 |  |  | -3572 | -3572 | -3572 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 397
20250612 | June | 1630 | 6761 |  |  | 6761 |  |  | -3572 | -3572 | -3572 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 401 |  |  |  |  | FR | 3525 | Process fail during TSO validation phase
20250612 | June | 1730 | 6761 |  |  | 6761 |  |  | -3572 | -3572 | -3572 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 395 |  |  |  |  | FR | 3525 | Process fail during TSO validation phase
20250612 | June | 1830 |  | 6421 | 630 | 6872 |  |  | 2590 | 168 | 3331 | Minimum Margin | TTC Validation phase - bilateral reduction | 1200 | NA | 0 |  |  | AT | 395 |  |  |  |  | FR | 3525 | Process fail during TSO validation phase
20250612 | June | 1930 |  | 6338 | 621 | 6833 |  |  | 2590 | 85 | 3333 | Minimum Margin | TTC Validation phase - bilateral reduction | 1309 | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 2030 |  | 6338 | 621 | 6833 |  |  | 2590 | 85 | 3333 | Minimum Margin | TTC Validation phase - bilateral reduction | 1409 | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250612 | June | 2130 |  | 8174 | 705 | 8250 |  |  | -2191 | -2191 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1425 | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250612 | June | 2230 |  | 8174 | 705 | 8250 |  |  | -2191 | -2191 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1525 | NA | 0 |  |  | AT | 401
20250612 | June | 2330 |  | 7796 | 730 | 7850 |  |  | -1759 | -1759 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1600 | NA | 0 |  |  | AT | 401
20250613 | June | 30 | 7612 |  |  | 7412 |  |  | -3765 | -3765 | -3565 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 401
20250613 | June | 130 | 7612 |  |  | 7412 |  |  | -3765 | -3765 | -3565 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250613 | June | 230 | 7612 |  |  | 7412 |  |  | -3765 | -3765 | -3565 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250613 | June | 330 | 8492 |  |  | 8329 |  |  | -5501 | -5501 | -5349 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250613 | June | 430 | 8492 |  |  | 8329 |  |  | -5501 | -5501 | -5349 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250613 | June | 530 | 8492 |  |  | 8329 |  |  | -5501 | -5501 | -5349 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250613 | June | 630 | 8292 |  |  | 8129 |  |  | -5293 | -5293 | -5141 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 418
20250613 | June | 730 | 8339 |  |  | 8168 |  |  | -2951 | -2951 | -2782 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 334
20250613 | June | 830 | 8339 |  |  | 7989 |  |  | -2951 | -2951 | -2606 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 337
20250613 | June | 930 | 6490 |  |  | 6489 |  |  | 4521 | 25 | 4497 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 337
20250613 | June | 1030 | 6536 |  |  | 6535 |  |  | 4521 | 71 | 4451 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 342
20250613 | June | 1130 | 6534 |  |  | 6534 |  |  | 4521 | 69 | 4453 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 342
20250613 | June | 1230 | 6632 |  |  | 6631 |  |  | -822 | -822 | -821 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 342
20250613 | June | 1330 | 6632 |  |  | 6631 |  |  | -822 | -822 | -821 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421
20250613 | June | 1430 | 6632 |  |  | 6631 |  |  | -822 | -822 | -821 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421
20250613 | June | 1530 | 8031 |  |  | 8031 |  |  | -3528 | -3528 | -3528 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421
20250613 | June | 1630 | 8031 |  |  | 8031 |  |  | -3528 | -3528 | -3528 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 409
20250613 | June | 1730 | 8031 |  |  | 8031 |  |  | -3528 | -3528 | -3528 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 409
20250613 | June | 1830 | 8470 |  |  |  | 8190 | 644 | -2665 | -2665 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | -6902 |  |  | AT | 409
20250613 | June | 1930 | 8470 |  |  |  | 8190 | 644 | -2665 | -2665 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | -6902 |  |  | AT | 421
20250613 | June | 2030 | 8470 |  |  |  | 8190 | 644 | -2665 | -2665 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | -6902 |  |  | AT | 421
20250613 | June | 2130 | 8974 |  |  | 8619 |  |  | -6430 | -6430 | -6075 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 411
20250613 | June | 2230 | 8974 |  |  | 8619 |  |  | -6430 | -6430 | -6075 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250613 | June | 2330 | 8374 |  |  | 8019 |  |  | -5826 | -5826 | -5471 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 30 | 9276 |  |  | 8692 |  |  | -2495 | -2495 | -1913 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 130 | 9276 |  |  | 8692 |  |  | -2495 | -2495 | -1913 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 230 | 9276 |  |  | 8692 |  |  | -2495 | -2495 | -1913 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 330 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 430 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 530 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 387
20250614 | June | 630 | 9424 |  |  | 8969 |  |  | -5857 | -5857 | -5399 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 387
20250614 | June | 730 | 8289 |  |  | 8289 |  |  | -1720 | -1720 | -1720 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250614 | June | 830 | 8289 |  |  | 8289 |  |  | -1720 | -1720 | -1720 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250614 | June | 930 | 8428 |  |  | 8428 |  |  | -1545 | -1545 | -1545 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250614 | June | 1030 | 8428 |  |  | 8428 |  |  | -1545 | -1545 | -1545 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 345
20250614 | June | 1130 | 8428 |  |  | 8428 |  |  | -1545 | -1545 | -1545 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 345
20250614 | June | 1230 | 7441 |  |  | 7441 |  |  | -1559 | -1559 | -1559 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 345
20250614 | June | 1330 | 7441 |  |  | 7441 |  |  | -1559 | -1559 | -1559 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 419
20250614 | June | 1430 | 7441 |  |  | 7441 |  |  | -1559 | -1559 | -1559 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425
20250614 | June | 1530 | 9065 |  |  | 8941 |  |  | -2997 | -2997 | -2874 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425
20250614 | June | 1630 | 9065 |  |  | 8984 |  |  | -2997 | -2997 | -2916 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250614 | June | 1730 | 9065 |  |  | 8984 |  |  | -2997 | -2997 | -2916 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250614 | June | 1830 |  | 8641 | 668 |  | 8633 | 668 | -238 | -238 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1162 | NA | -7297 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250614 | June | 1930 |  | 8641 | 668 |  | 8633 | 668 | -238 | -238 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1262 | NA | -7297 |  |  | AT | 425
20250614 | June | 2030 |  | 8641 | 668 |  | 8633 | 668 | -238 | -238 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1362 | NA | -7297 |  |  | AT | 425
20250614 | June | 2130 | 9057 |  |  | 9057 |  |  | -2582 | -2582 | -2582 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250614 | June | 2230 | 9057 |  |  | 9057 |  |  | -2582 | -2582 | -2582 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250614 | June | 2330 | 8457 |  |  | 8457 |  |  | -1964 | -1964 | -1964 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 30 | 8910 |  |  | 8858 |  |  | -3702 | -3702 | -3659 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 130 | 8910 |  |  | 8858 |  |  | -3702 | -3702 | -3659 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 230 | 8910 |  |  | 8858 |  |  | -3702 | -3702 | -3659 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 330 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 430 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 530 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 630 | 9090 |  |  | 9023 |  |  | -3673 | -3673 | -3619 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 730 | 8865 |  |  | 8843 |  |  | -3326 | -3326 | -3314 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 830 | 8865 |  |  | 8843 |  |  | -3326 | -3326 | -3314 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 930 | 8562 |  |  | 8556 |  |  | -1834 | -1834 | -1830 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1030 | 8562 |  |  | 8556 |  |  | -1834 | -1834 | -1830 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250615 | June | 1130 | 8562 |  |  | 8556 |  |  | -1834 | -1834 | -1830 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250615 | June | 1230 | 8054 |  |  | 8054 |  |  | -1498 | -1498 | -1497 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 394
20250615 | June | 1330 | 8054 |  |  | 8054 |  |  | -1498 | -1498 | -1497 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1430 | 8054 |  |  | 8054 |  |  | -1498 | -1498 | -1497 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1530 | 9042 |  |  | 9011 |  |  | -1795 | -1795 | -1769 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1630 | 9042 |  |  | 9011 |  |  | -1795 | -1795 | -1769 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1730 | 9042 |  |  | 9011 |  |  | -1795 | -1795 | -1769 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1830 |  | 8373 | 731 |  | 8348 | 731 | -3476 | -3476 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1099 | NA | -6886 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 1930 |  | 8373 | 731 |  | 8348 | 731 | -3476 | -3476 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1199 | NA | -6886 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 2030 |  | 8373 | 731 |  | 8348 | 731 | -3476 | -3476 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1299 | NA | -6886 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 2130 |  | 8443 | 736 |  | 8127 | 710 | -3957 | -3957 | 0 | Critical Branch | Validation phase | 1394 | NA | -6707 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 2230 |  | 8443 | 736 |  | 8127 | 710 | -3957 | -3957 | 0 | Critical Branch | Validation phase | 1494 | NA | -6707 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250615 | June | 2330 |  | 8443 | 736 |  | 8127 | 710 | -3957 | -3957 | 0 | Critical Branch | Validation phase | 1594 | NA | -6707 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 30 | 9070 |  |  | 8450 |  |  | -2094 | -2094 | -1474 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 130 | 9070 |  |  | 8450 |  |  | -2094 | -2094 | -1474 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 230 | 9070 |  |  | 8450 |  |  | -2094 | -2094 | -1474 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 330 |  | 8643 | 812 |  | 7925 | 750 | -1902 | -1902 | 0 | Critical Branch | Validation phase | -482 | NA | -6425 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 430 |  | 8643 | 812 |  | 7925 | 750 | -1902 | -1902 | 0 | Critical Branch | Validation phase | -382 | NA | -6425 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 530 |  | 8643 | 812 |  | 7925 | 750 | -1902 | -1902 | 0 | Critical Branch | Validation phase | -282 | NA | -6425 |  |  | AT | 412
20250616 | June | 630 |  | 8442 | 812 |  | 7724 | 750 | -1651 | -1651 | 0 | Critical Branch | Validation phase | -182 | NA | -6224 |  |  | AT | 399
20250616 | June | 730 | 8653 |  |  | 8652 |  |  | -2048 | -2048 | -2048 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 323
20250616 | June | 830 | 8653 |  |  | 7750 |  |  | -2048 | -2048 | -1147 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 323
20250616 | June | 930 | 6890 |  |  | 6250 |  |  | 2751 | 160 | 3231 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 323
20250616 | June | 1030 | 6890 |  |  | 6250 |  |  | 2751 | 160 | 3231 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 348
20250616 | June | 1130 | 6890 |  |  | 6250 |  |  | 2751 | 160 | 3231 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 348
20250616 | June | 1230 | 7379 |  |  | 7379 |  |  | 4155 | 160 | 3995 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 348
20250616 | June | 1330 | 7379 |  |  | 7379 |  |  | 4155 | 160 | 3995 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 325
20250616 | June | 1430 | 7379 |  |  | 7379 |  |  | 4155 | 160 | 3995 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 325
20250616 | June | 1530 | 6935 |  |  | 6934 |  |  | 2737 | 153 | 2584 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 325
20250616 | June | 1630 | 6935 |  |  | 6934 |  |  | 2737 | 153 | 2584 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 360
20250616 | June | 1730 | 6935 |  |  | 6934 |  |  | 2737 | 153 | 2584 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 360
20250616 | June | 1830 |  | 7272 | 586 |  | 7271 | 586 | -1747 | -1747 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1244 | NA | -6099 |  |  | AT | 360
20250616 | June | 1930 |  | 7272 | 586 |  | 7271 | 586 | -1747 | -1747 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1344 | NA | -6099 |  |  | AT | 340
20250616 | June | 2030 |  | 7272 | 586 |  | 7271 | 586 | -1747 | -1747 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1444 | NA | -6099 |  |  | AT | 340
20250616 | June | 2130 |  | 6898 | 547 |  | 6897 | 547 | -1115 | -1115 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1583 | NA | -5803 |  |  | AT | 325
20250616 | June | 2230 |  | 6898 | 547 |  | 6897 | 547 | -1115 | -1115 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1683 | NA | -5803 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250616 | June | 2330 |  | 6317 | 572 |  | 6316 | 572 | -494 | -494 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1758 | NA | -5172 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250617 | June | 30 | 8949 |  |  | 8736 |  |  | -4866 | -4866 | -4649 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250617 | June | 130 | 8949 |  |  | 8736 |  |  | -4866 | -4866 | -4649 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250617 | June | 230 | 8949 |  |  | 8736 |  |  | -4866 | -4866 | -4649 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250617 | June | 330 | 8675 |  |  | 8663 |  |  | -4708 | -4708 | -4693 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250617 | June | 430 | 8675 |  |  | 8663 |  |  | -4708 | -4708 | -4693 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250617 | June | 530 | 8675 |  |  | 8663 |  |  | -4708 | -4708 | -4693 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 339
20250617 | June | 630 | 8475 |  |  | 8463 |  |  | -4500 | -4500 | -4485 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 339
20250617 | June | 730 | 7219 |  |  | 7218 |  |  | -2023 | -2023 | -2023 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 315
20250617 | June | 830 | 7219 |  |  | 7218 |  |  | -2023 | -2023 | -2023 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 315
20250617 | June | 930 | 6730 |  |  | 6730 |  |  | -3515 | -3515 | -3514 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 315
20250617 | June | 1030 | 6730 |  |  | 6730 |  |  | -3515 | -3515 | -3514 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250617 | June | 1130 | 6730 |  |  | 6730 |  |  | -3515 | -3515 | -3514 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1230 | 8900 |  |  | 8230 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1330 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1430 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1530 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1630 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1730 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1830 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 1930 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 2030 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 425
20250617 | June | 2130 | 9050 |  |  | 9050 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | NA | NA | 0 |  |  | AT | 415
20250618 | June | 1730 | 8782 |  |  | 8502 |  |  | -1640 | -1640 | -1361 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp
20250618 | June | 2230 |  | 7516 | 581 |  | 7516 | 581 | -5544 | -5544 | 0 | Critical Branch | Critical Branch | 1649 | NA | -6354 |  |  | AT | 415
20250618 | June | 2330 |  | 6956 | 606 |  | 6956 | 606 | -4922 | -4922 | 0 | Critical Branch | Critical Branch | 1724 | NA | -5744 |  |  | AT | 415
20250619 | June | 30 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250619 | June | 130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250619 | June | 230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250619 | June | 330 | 8956 |  |  | 8888 |  |  | -6022 | -6022 | -5965 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250619 | June | 430 | 8956 |  |  | 8888 |  |  | -6022 | -6022 | -5965 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250619 | June | 530 | 8956 |  |  | 8888 |  |  | -6022 | -6022 | -5965 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 383
20250619 | June | 630 | 8756 |  |  | 8687 |  |  | -5809 | -5809 | -5751 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 382
20250619 | June | 730 | 8074 |  |  | 8074 |  |  | 3301 | 157 | 3144 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250619 | June | 830 | 8053 |  |  | 8053 |  |  | 3301 | 136 | 3165 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250619 | June | 930 | 7563 |  |  | 7563 |  |  | -478 | -478 | -478 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 357
20250619 | June | 1030 | 7563 |  |  | 7563 |  |  | -478 | -478 | -478 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 321
20250619 | June | 1130 | 7563 |  |  | 7563 |  |  | -478 | -478 | -478 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 321
20250619 | June | 1230 | 6858 |  |  | 6857 |  |  | -850 | -850 | -849 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 321
20250619 | June | 1330 | 6858 |  |  | 6857 |  |  | -850 | -850 | -849 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 315
20250619 | June | 1430 | 6858 |  |  | 6857 |  |  | -850 | -850 | -849 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 315
20250619 | June | 1530 | 6730 |  |  | 6730 |  |  | -3532 | -3532 | -3532 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 315
20250619 | June | 1630 | 6730 |  |  | 6730 |  |  | -3532 | -3532 | -3532 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 384
20250619 | June | 1730 | 6730 |  |  | 6730 |  |  | -3532 | -3532 | -3532 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250619 | June | 1830 |  | 8546 | 661 |  | 7717 | 661 | 1195 | 155 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1169 | NA | -6395 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250619 | June | 1930 |  | 8856 | 685 |  | 8836 | 685 | 1195 | 465 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1245 | NA | -7466 |  |  | AT | 410
20250619 | June | 2030 |  | 8856 | 685 |  | 8836 | 685 | 1195 | 465 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1345 | NA | -7466 |  |  | AT | 410
20250619 | June | 2130 | 8757 |  |  | 8757 |  |  | -2348 | -2348 | -2348 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 399
20250620 | June | 1230 | 8900 |  |  | 7879 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 7629 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1330 | 8900 |  |  | 7879 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 7629 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1430 | 8900 |  |  | 7879 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 7629 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1530 | 8900 |  |  | 7704 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 7454 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1630 | 8900 |  |  | 7704 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 7454 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 1730 | 8900 |  |  | 7704 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 | [11 empty] | SI | 7454 | Overload: CNEC: CNE: 400 kV DivacaRedipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered
20250620 | June | 2230 | 9050 |  |  | 8550 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250620 | June | 2330 | 8450 |  |  | 7950 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 30 | 9088 |  |  | 9055 |  |  | -2594 | -2594 | -2567 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 130 | 9088 |  |  | 9055 |  |  | -2594 | -2594 | -2567 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 230 | 9088 |  |  | 9055 |  |  | -2594 | -2594 | -2567 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 330 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 430 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 530 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 394
20250621 | June | 630 | 8791 |  |  | 8768 |  |  | -3073 | -3073 | -3059 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 394
20250621 | June | 730 | 8437 |  |  | 8436 |  |  | -4975 | -4975 | -4974 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250621 | June | 830 | 8437 |  |  | 8436 |  |  | -4975 | -4975 | -4974 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250621 | June | 930 | 8158 |  |  | 8157 |  |  | -579 | -579 | -578 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250621 | June | 1030 | 8158 |  |  | 8157 |  |  | -579 | -579 | -578 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 326
20250621 | June | 1130 | 8158 |  |  | 8157 |  |  | -579 | -579 | -578 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 326
20250621 | June | 1230 | 7067 |  |  | 7067 |  |  | 187 | 187 | 1 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 326
20250621 | June | 1330 | 7067 |  |  | 7067 |  |  | 187 | 187 | 1 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250621 | June | 1430 | 7067 |  |  | 7067 |  |  | 187 | 187 | 1 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250621 | June | 1530 | 8161 |  |  | 8160 |  |  | -1167 | -1167 | -1166 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250621 | June | 1630 | 8161 |  |  | 8160 |  |  | -1167 | -1167 | -1166 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3588 | Process fail during TSO validation phase
20250621 | June | 1730 | 8161 |  |  | 8160 |  |  | -1167 | -1167 | -1166 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 421 |  |  |  |  | FR | 3588 | Process fail during TSO validation phase
20250621 | June | 1830 |  | 8414 | 651 |  | 8192 | 651 | 2048 | 461 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1179 | NA | -6890 |  |  | AT | 421 |  |  |  |  | FR | 3588 | Process fail during TSO validation phase
20250621 | June | 1930 |  | 8414 | 651 |  | 8192 | 651 | 2048 | 461 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1279 | NA | -6890 |  |  | AT | 360
20250621 | June | 2030 |  | 8414 | 651 |  | 8192 | 651 | 2048 | 461 | 0 | Minimum Margin | TTC Validation phase - bilateral reduction | 1379 | NA | -6890 |  |  | AT | 360
20250621 | June | 2130 |  | 7266 | 561 |  | 7266 | 561 | -3761 | -3761 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1569 | NA | -6144 |  |  | AT | 347
20250621 | June | 2230 |  | 7266 | 561 |  | 7266 | 561 | -3761 | -3761 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1669 | NA | -6144 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250621 | June | 2330 |  | 6706 | 586 |  | 6706 | 586 | -3179 | -3179 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1744 | NA | -5534 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 30 | 8873 |  |  | 8500 |  |  | -1927 | -1927 | -1561 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 130 | 8873 |  |  | 8500 |  |  | -1927 | -1927 | -1561 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 230 | 8873 |  |  | 8500 |  |  | -1927 | -1927 | -1561 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 330 | 8687 |  |  | 8373 |  |  | 1145 | 573 | 872 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 430 | 8489 |  |  | 8389 |  |  | 1145 | 375 | 856 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 530 | 8687 |  |  | 8373 |  |  | 1145 | 573 | 872 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 630 | 8529 |  |  | 8393 |  |  | 1145 | 415 | 851 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 730 | 8870 |  |  | 8764 |  |  | -624 | -624 | -524 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 372
20250622 | June | 830 | 8870 |  |  | 8004 |  |  | -624 | -624 | 237 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 372
20250622 | June | 930 | 7089 |  |  | 6504 |  |  | -11 | -11 | 574 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 372
20250622 | June | 1030 | 7089 |  |  | 6504 |  |  | -11 | -11 | 574 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 375
20250622 | June | 1130 | 7089 |  |  | 6504 |  |  | -11 | -11 | 574 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 365
20250622 | June | 1230 | 7151 |  |  | 6402 |  |  | 596 | 463 | 882 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 379
20250622 | June | 1330 | 6967 |  |  | 6402 |  |  | 596 | 279 | 882 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 1430 | 7226 |  |  | 6402 |  |  | 596 | 538 | 882 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 1530 |  | 7795 | 774 |  | 7617 | 769 | -694 | -694 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 756 | NA | -6079 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 1630 |  | 7795 | 774 |  | 7714 | 769 | -694 | -694 | 0 | Critical Branch | Validation phase | 856 | NA | -6176 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 1730 |  | 7795 | 774 |  | 7714 | 769 | -694 | -694 | 0 | Critical Branch | Validation phase | 956 | NA | -6176 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 1830 |  | 8600 | 821 |  | 8120 | 781 | -6213 | -6213 | 0 | Critical Branch | Validation phase | 1009 | NA | -6558 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 1930 |  | 8600 | 821 |  | 8120 | 781 | -6213 | -6213 | 0 | Critical Branch | Validation phase | 1109 | NA | -6558 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 2030 |  | 8600 | 821 |  | 8120 | 781 | -6213 | -6213 | 0 | Critical Branch | Validation phase | 1209 | NA | -6558 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 2130 |  | 8629 | 827 |  | 8120 | 784 | -6623 | -6623 | 0 | Critical Branch | Validation phase | 1303 | NA | -6552 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 2230 |  | 8629 | 827 |  | 8120 | 784 | -6623 | -6623 | 0 | Critical Branch | Validation phase | 1403 | NA | -6552 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250622 | June | 2330 |  | 8629 | 827 |  | 8120 | 784 | -6623 | -6623 | 0 | Critical Branch | Validation phase | 1503 | NA | -6552 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 30 | 8675 |  |  | 8300 |  |  | -4904 | -4904 | -4539 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 130 | 8675 |  |  | 8300 |  |  | -4904 | -4904 | -4539 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 230 | 8675 |  |  | 8300 |  |  | -4904 | -4904 | -4539 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 330 | 8193 |  |  | 8078 |  |  | -2870 | -2870 | -2761 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 430 | 8193 |  |  | 8078 |  |  | -2870 | -2870 | -2761 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 530 | 8193 |  |  | 8078 |  |  | -2870 | -2870 | -2761 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 203
20250623 | June | 630 | 7993 |  |  | 7878 |  |  | -2649 | -2649 | -2540 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 202
20250623 | June | 730 | 7861 |  |  | 6577 |  |  | -1623 | -1623 | -339 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250623 | June | 830 | 6861 |  |  | 5577 |  |  | -474 | -474 | 810 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250623 | June | 930 | 7560 |  |  | 6277 |  |  | -961 | -961 | 322 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250623 | June | 1030 | 7560 |  |  | 6277 |  |  | -961 | -961 | 322 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 198
20250623 | June | 1130 | 7560 |  |  | 6277 |  |  | -961 | -961 | 322 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 195
20250623 | June | 1230 | 6725 |  |  | 5155 |  |  | 227 | 227 | 1570 | Adjustment reached | Validation phase | NA | NA | 0 |  |  | AT | 198
20250623 | June | 1330 | 6617 |  |  | 5155 |  |  | 227 | 119 | 1570 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250623 | June | 1430 | 6725 |  |  | 5155 |  |  | 227 | 227 | 1570 | Adjustment reached | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250623 | June | 1530 | 7950 |  |  | 6655 |  |  | -1231 | -1231 | 64 | Critical Branch | Smoothing ramp | NA | NA | 0 | Smoothing | Smoothing ramp | AT | 425 | Reduction because NTC over thermal limit on border
20250623 | June | 1630 | 7950 |  |  | 6810 |  |  | -1231 | -1231 | -91 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250623 | June | 1730 | 9165 |  |  | 8025 |  |  | -2604 | -2604 | -1464 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250623 | June | 1830 |  | 8632 | 734 |  | 8358 | 714 | -1577 | -1577 | 0 | Critical Branch | Validation phase | 1096 | NA | -6930 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250623 | June | 1930 |  | 8632 | 734 |  | 8358 | 714 | -1577 | -1577 | 0 | Critical Branch | Validation phase | 1196 | NA | -6930 |  |  | AT | 425
20250623 | June | 2030 |  | 8632 | 734 |  | 8358 | 714 | -1577 | -1577 | 0 | Critical Branch | Validation phase | 1296 | NA | -6930 |  |  | AT | 425
20250623 | June | 2130 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250623 | June | 2230 | 8450 |  |  | 8450 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250623 | June | 2330 | 7850 |  |  | 7850 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250624 | June | 30 | 8261 |  |  | 7840 |  |  | -1695 | -1695 | -1274 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250624 | June | 130 | 8261 |  |  | 7840 |  |  | -1695 | -1695 | -1274 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250624 | June | 230 | 8261 |  |  | 7840 |  |  | -1695 | -1695 | -1274 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250624 | June | 330 | 8115 |  |  | 7729 |  |  | -1563 | -1563 | -1177 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250624 | June | 430 | 8115 |  |  | 7729 |  |  | -1563 | -1563 | -1177 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250624 | June | 530 | 8115 |  |  | 7729 |  |  | -1563 | -1563 | -1177 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 414
20250624 | June | 630 | 7915 |  |  | 7529 |  |  | -1337 | -1337 | -951 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 414
20250624 | June | 730 | 7134 |  |  | 6838 |  |  | -1034 | -1034 | -738 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 336
20250624 | June | 830 | 7134 |  |  | 6838 |  |  | -1034 | -1034 | -738 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 351
20250624 | June | 930 | 5881 |  |  | 5750 |  |  | 421 | 0 | 552 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 341
20250624 | June | 1030 | 6123 |  |  | 5750 |  |  | 421 | 242 | 552 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 320
20250624 | June | 1130 | 5963 |  |  | 5750 |  |  | 421 | 82 | 552 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 309
20250624 | June | 1230 | 5635 |  |  | 4638 |  |  | 693 | 186 | 1504 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 323
20250624 | June | 1330 | 5449 |  |  | 4638 |  |  | 693 | 0 | 1504 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 309
20250624 | June | 1430 | 5681 |  |  | 4638 |  |  | 693 | 232 | 1504 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 315
20250624 | June | 1530 | 5451 |  |  | 4536 |  |  | 785 | 155 | 1545 | Minimum Margin | Validation phase | NA | NA | 0 |  |  | AT | 315
20250624 | June | 1630 | 6296 |  |  | 5536 |  |  | -341 | -341 | 419 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 404
20250624 | June | 1730 | 6296 |  |  | 5536 |  |  | -341 | -341 | 419 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250624 | June | 1830 |  | 8254 | 698 |  | 6782 | 698 | -2495 | -2495 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1132 | NA | -5386 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250624 | June | 1930 |  | 8254 | 698 |  | 8232 | 698 | -2495 | -2495 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1232 | NA | -6836 |  |  | AT | 405
20250624 | June | 2030 |  | 8254 | 698 |  | 8233 | 698 | -2495 | -2495 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1332 | NA | -6837 |  |  | AT | 405
20250624 | June | 2130 | 8092 |  |  | 7754 |  |  | -1681 | -1681 | -1343 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 394
20250625 | June | 330 | 8107 |  |  | 7925 |  |  | -440 | -440 | -258 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7675 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 430 | 8107 |  |  | 7925 |  |  | -440 | -440 | -258 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7675 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 530 | 8107 |  |  | 7925 |  |  | -440 | -440 | -258 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7675 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 630 | 7907 |  |  | 7725 |  |  | -207 | -207 | -25 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7475 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 1230 | 7739 |  |  | 7341 |  |  | -431 | -431 | -33 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7091 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 1330 | 7739 |  |  | 7341 |  |  | -431 | -431 | -33 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7091 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 1430 | 7739 |  |  | 7341 |  |  | -431 | -431 | -33 | Critical Branch | Validation phase | NA | NA | 0 | [5 empty] | CH | 7091 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20250625 | June | 2230 |  | 7689 | 624 |  | 7689 | 624 | -5123 | -5123 | 0 | Critical Branch | Critical Branch | 1606 | NA | -6441 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250625 | June | 2330 |  | 7109 | 649 |  | 7109 | 649 | -4495 | -4495 | 0 | Critical Branch | Critical Branch | 1681 | NA | -5811 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 30 | 9498 |  |  | 9332 |  |  | -6088 | -6088 | -5940 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 130 | 9498 |  |  | 9332 |  |  | -6088 | -6088 | -5940 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 230 | 9498 |  |  | 9332 |  |  | -6088 | -6088 | -5940 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 330 | 8611 |  |  | 8542 |  |  | -4953 | -4953 | -4886 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 430 | 8611 |  |  | 8542 |  |  | -4953 | -4953 | -4886 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 530 | 8611 |  |  | 8542 |  |  | -4953 | -4953 | -4886 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 630 | 8411 |  |  | 8342 |  |  | -4747 | -4747 | -4679 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 730 | 8248 |  |  | 8191 |  |  | -1641 | -1641 | -1595 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 830 | 8248 |  |  | 8191 |  |  | -1641 | -1641 | -1595 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 930 | 7667 |  |  | 7657 |  |  | -1056 | -1056 | -1047 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1030 | 7667 |  |  | 7657 |  |  | -1056 | -1056 | -1047 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 406
20250626 | June | 1130 | 7667 |  |  | 7657 |  |  | -1056 | -1056 | -1047 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 406
20250626 | June | 1230 | 7196 |  |  | 7195 |  |  | -600 | -600 | -599 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 406
20250626 | June | 1330 | 7196 |  |  | 7195 |  |  | -600 | -600 | -599 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1430 | 7196 |  |  | 7195 |  |  | -600 | -600 | -599 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1530 | 7623 |  |  | 7616 |  |  | -1232 | -1232 | -1225 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1630 | 7623 |  |  | 7616 |  |  | -1232 | -1232 | -1225 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1730 | 9023 |  |  | 9017 |  |  | -2910 | -2910 | -2904 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1830 | 9645 |  |  | 9086 |  |  | -1989 | -1989 | -1430 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 1930 | 9645 |  |  | 9086 |  |  | -1989 | -1989 | -1430 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 2030 | 9645 |  |  | 9086 |  |  | -1989 | -1989 | -1430 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250626 | June | 2130 | 9673 |  |  | 8975 |  |  | -2568 | -2568 | -1870 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 2230 | 9673 |  |  | 8975 |  |  | -2568 | -2568 | -1870 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250626 | June | 2330 | 9073 |  |  | 8375 |  |  | -1946 | -1946 | -1248 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250627 | June | 30 | 9115 |  |  | 8753 |  |  | -5089 | -5089 | -4734 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250627 | June | 130 | 9115 |  |  | 8753 |  |  | -5089 | -5089 | -4734 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 406
20250627 | June | 230 | 9115 |  |  | 8753 |  |  | -5089 | -5089 | -4734 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 406
20250627 | June | 330 | 8283 |  |  | 8227 |  |  | -4041 | -4041 | -3985 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 406
20250627 | June | 430 | 8283 |  |  | 8227 |  |  | -4041 | -4041 | -3985 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 406
20250627 | June | 530 | 8283 |  |  | 8227 |  |  | -4041 | -4041 | -3985 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 402
20250627 | June | 630 | 8083 |  |  | 8027 |  |  | -3826 | -3826 | -3770 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 402
20250627 | June | 730 | 8455 |  |  | 8417 |  |  | -4731 | -4731 | -4693 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 338
20250627 | June | 830 | 8455 |  |  | 8417 |  |  | -4731 | -4731 | -4693 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 338
20250627 | June | 930 | 7200 |  |  | 7199 |  |  | -3620 | -3620 | -3618 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 338
20250627 | June | 1030 | 7200 |  |  | 7199 |  |  | -3620 | -3620 | -3618 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 414
20250627 | June | 1130 | 7200 |  |  | 7199 |  |  | -3620 | -3620 | -3618 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415
20250627 | June | 1230 | 8705 |  |  | 8620 |  |  | -750 | -750 | -665 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415
20250627 | June | 1330 | 8705 |  |  | 8620 |  |  | -750 | -750 | -665 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 422
20250627 | June | 1430 | 8705 |  |  | 8620 |  |  | -750 | -750 | -665 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 422
20250627 | June | 1530 | 8851 |  |  | 8678 |  |  | -4595 | -4595 | -4422 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 422
20250627 | June | 1630 | 8851 |  |  | 8678 |  |  | -4595 | -4595 | -4422 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 393
20250627 | June | 1730 | 8851 |  |  | 8678 |  |  | -4595 | -4595 | -4422 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 393
20250627 | June | 1830 |  | 7895 | 634 |  | 7894 | 634 | -4990 | -4990 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1196 | NA | -6626 |  |  | AT | 393
20250627 | June | 1930 |  | 7895 | 634 |  | 7894 | 634 | -4990 | -4990 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1296 | NA | -6626 |  |  | AT | 408
20250627 | June | 2030 |  | 7895 | 634 |  | 7894 | 634 | -4990 | -4990 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1396 | NA | -6626 |  |  | AT | 408
20250627 | June | 2130 |  | 8166 | 663 |  | 8166 | 663 | -5565 | -5565 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1467 | NA | -6840 |  |  | AT | 396
20250627 | June | 2230 |  | 8166 | 663 |  | 8166 | 663 | -5565 | -5565 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1567 | NA | -6840 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250627 | June | 2330 |  | 7586 | 688 |  | 7586 | 688 | -4933 | -4933 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1642 | NA | -6210 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 30 | 9269 |  |  | 8986 |  |  | -5728 | -5728 | -5456 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 130 | 9269 |  |  | 8986 |  |  | -5728 | -5728 | -5456 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 230 | 9269 |  |  | 8986 |  |  | -5728 | -5728 | -5456 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 330 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 430 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 530 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 630 | 9271 |  |  | 9009 |  |  | -3221 | -3221 | -2973 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 730 | 9102 |  |  | 9099 |  |  | -5936 | -5936 | -5933 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250628 | June | 830 | 9102 |  |  | 9099 |  |  | -5936 | -5936 | -5933 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250628 | June | 930 | 8164 |  |  | 8163 |  |  | -212 | -212 | -211 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 380
20250628 | June | 1030 | 8164 |  |  | 8163 |  |  | -212 | -212 | -211 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 350
20250628 | June | 1130 | 8164 |  |  | 8163 |  |  | -212 | -212 | -211 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 350
20250628 | June | 1230 | 7542 |  |  | 7542 |  |  | -433 | -433 | -432 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 350
20250628 | June | 1330 | 7542 |  |  | 7542 |  |  | -433 | -433 | -432 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250628 | June | 1430 | 7542 |  |  | 7542 |  |  | -433 | -433 | -432 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 391
20250628 | June | 1530 |  | 7845 | 629 |  | 7784 | 624 | -693 | -693 | 0 | Critical Branch | Validation phase | 901 | NA | -6536 |  |  | AT | 391
20250628 | June | 1630 |  | 7845 | 629 |  | 7784 | 624 | -693 | -693 | 0 | Critical Branch | Validation phase | 1001 | NA | -6536 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 1730 |  | 7845 | 629 |  | 7784 | 624 | -693 | -693 | 0 | Critical Branch | Validation phase | 1101 | NA | -6536 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 1830 |  | 8915 | 721 |  | 8892 | 721 | -2490 | -2490 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1109 | NA | -7450 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 1930 |  | 8915 | 721 |  | 8892 | 721 | -2490 | -2490 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1209 | NA | -7450 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 2030 |  | 8915 | 721 |  | 8892 | 721 | -2490 | -2490 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1309 | NA | -7450 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
20250628 | June | 2130 | 9229 |  |  | 8234 |  |  | -2487 | -2487 | -1492 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 2230 | 9229 |  |  | 8234 |  |  | -2487 | -2487 | -1492 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250628 | June | 2330 | 8629 |  |  | 7634 |  |  | -1871 | -1871 | -876 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 30 | 9304 |  |  | 8942 |  |  | -3681 | -3681 | -3331 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 130 | 9304 |  |  | 8942 |  |  | -3681 | -3681 | -3331 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 412
20250629 | June | 230 | 9304 |  |  | 8942 |  |  | -3681 | -3681 | -3331 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 412
20250629 | June | 330 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 412
20250629 | June | 430 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 412
20250629 | June | 530 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 630 | 8399 |  |  | 8399 |  |  | -4893 | -4893 | -4893 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 730 | 8870 |  |  | 8688 |  |  | -1915 | -1915 | -1735 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 374
20250629 | June | 830 | 8870 |  |  | 8688 |  |  | -1915 | -1915 | -1735 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 374
20250629 | June | 930 | 7665 |  |  | 7630 |  |  | -968 | -968 | -933 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 374
20250629 | June | 1030 | 7665 |  |  | 7630 |  |  | -968 | -968 | -933 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 352
20250629 | June | 1130 | 7665 |  |  | 7630 |  |  | -968 | -968 | -933 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 352
20250629 | June | 1230 | 7248 |  |  | 7225 |  |  | -766 | -766 | -743 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 352
20250629 | June | 1330 | 7248 |  |  | 7225 |  |  | -766 | -766 | -743 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 1430 | 7248 |  |  | 7225 |  |  | -766 | -766 | -743 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 1530 |  | 8130 | 720 |  | 8119 | 720 | -1871 | -1871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 810 | NA | -6679 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 1630 |  | 8130 | 720 |  | 8119 | 720 | -1871 | -1871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 910 | NA | -6679 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 1730 |  | 8130 | 720 |  | 8119 | 720 | -1871 | -1871 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1010 | NA | -6679 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 1830 | 9656 |  |  | 8385 |  |  | -5475 | -5475 | -4204 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 1930 | 9656 |  |  | 8385 |  |  | -5475 | -5475 | -4204 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 2030 | 9656 |  |  | 8385 |  |  | -5475 | -5475 | -4204 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 2130 | 9290 |  |  | 8345 |  |  | -5636 | -5636 | -4691 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
20250629 | June | 2230 | 9290 |  |  | 8345 |  |  | -5636 | -5636 | -4691 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250629 | June | 2330 | 9290 |  |  | 8345 |  |  | -5636 | -5636 | -4691 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 30 | 8402 |  |  | 7974 |  |  | -1203 | -1203 | -789 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 130 | 8402 |  |  | 7974 |  |  | -1203 | -1203 | -789 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 230 | 8402 |  |  | 7974 |  |  | -1203 | -1203 | -789 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 330 | 8628 |  |  | 8341 |  |  | -4469 | -4469 | -4256 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3000 | Planned outage of Piossasco-Grande-Ile 1 HVDC
20250630 | June | 430 | 8628 |  |  | 8341 |  |  | -4469 | -4469 | -4256 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3000 | Planned outage of Piossasco-Grande-Ile 1 HVDC
20250630 | June | 530 | 8628 |  |  | 7678 |  |  | -4469 | -4469 | -3330 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 630 | 8428 |  |  | 7476 |  |  | -4298 | -4298 | -3166 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 730 | 7383 |  |  | 7245 |  |  | -4170 | -4170 | -3967 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 830 | 7383 |  |  | 7245 |  |  | -4170 | -4170 | -3967 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 930 | 6899 |  |  | 6785 |  |  | -1687 | -1687 | -1569 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1030 | 6899 |  |  | 6785 |  |  | -1687 | -1687 | -1569 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1130 | 6899 |  |  | 6785 |  |  | -1687 | -1687 | -1569 | Critical Branch | TTC Validation phase - bilateral reduction | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1230 | 6730 |  |  | 6377 |  |  | -1219 | -1219 | -865 | TTC Selection - LTTC | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1330 | 6730 |  |  | 6377 |  |  | -1219 | -1219 | -865 | TTC Selection - LTTC | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1430 | 6730 |  |  | 6377 |  |  | -1219 | -1219 | -865 | TTC Selection - LTTC | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1530 | 7306 |  |  | 6386 |  |  | -313 | -313 | 609 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1630 | 7306 |  |  | 6386 |  |  | -313 | -313 | 609 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1730 | 7306 |  |  | 6386 |  |  | -313 | -313 | 609 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1830 | 8202 |  |  | 7459 |  |  | -966 | -966 | -229 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 1930 | 8202 |  |  | 7459 |  |  | -966 | -966 | -229 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 2030 | 8202 |  |  | 7459 |  |  | -966 | -966 | -229 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border
20250630 | June | 2130 | 8527 |  |  | 7778 |  |  | -1394 | -1394 | -654 | Critical Branch | Validation phase | NA | NA | 0 |  |  | AT | 210 | Reduction because NTC over thermal limit on border

## DA FLAGS processing
FLAGS processing
TSO | Long description | Short | Type | # of TS | CB | CO
AT | Reduction because NTC over thermal limit on border | Reduction because NTC over thermal limit on border | NTC over thermal limit | 906
CH | Reduction due to missing redispatch potential | Reduction due to missing redispatch potential | Redispatch | 228
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 113 | CNE: 380kV Lavorgo - Musignano [DIR] [CH], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | Expected overloading on the following CNEC: CNE: 380kV Pradella-Robbia [DIR], C: N-2 Pradella-Sils + Filisur-Sils | CNEC: CNE: 380kV Pradella-Robbia [DIR], C: N-2 Pradella-Sils + Filisur-Sils | Overload | 6 | CNE: 380kV Pradella-Robbia [DIR], | -2 Pradella-Sils + Filisur-Sils
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 21 | CNE: 380kV Lavorgo - Musignano [DIR] [CH], | -2 Pradella-Robbia + Filisur-Robbia
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT issues | 304
CH | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 RONDISSONE-TRINO | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 RONDISSONE-TRINO | Outage | 12
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | Overload | 8
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 17 | CNE: 380kV Bulciago - Soazza [DIR] [CH], | -2 Pradella-Robbia + Filisur-Robbia
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | Overload | 41 | CNE: 380kV Fiorano-Robbia [DIR][IT], | 80KV GORLAGO-ROBBIA
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 36 | CNE: 220kV Riddes - Valpelline [DIR] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Pradella-Sils | CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Pradella-Sils | Overload | 6 | CNE: 380kV Bulciago - Soazza [DIR] [CH], | -2 Pradella-Robbia + Pradella-Sils
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 6 | CNE: 220kV Avise - Riddes [OPP] [CH], | -2 ALBERTVILLE-RONDISSONE
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 37 | CNE: 380kV Bulciago - Soazza [DIR] [CH], | -2 Robbia-Gorlago + Robbia-S.Fiorano
CH | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 PRADELLA-ROBBIA | Outage | 6
CH | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | Missing CNEC in CC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 PRAD-ROBB + FILISUR-ROBBIA + CRA_PRADELLA_SILS | Outage | 3
FR | Planned outage of Creys-Saint-Vulbas 2 | Planned outage of Creys-Saint-Vulbas 2 | Outage | 91
FR | Process fail during TSO validation phase | Process fail during TSO validation phase | Process Fail | 119
FR | N-1 Chaffard-Grande Ile 1 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | N-1 Chaffard-Grande Ile 1 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | Outage | 3
FR | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | N-1 Creys-Saint Vulbas 2 / [FR-FR] Creys-Saint Vulbas 1 [OPP] [FR] | Outage | 7
FR | Planned outage of Chaffard-Grande-Ile 2 | Planned outage of Chaffard-Grande-Ile 2 | Outage | 187
FR | Process failed: missing input | Process failed: missing input | Process Fail | 120
FR | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | N-1 Creys-Saint Vulbas 1 / [FR-FR] Creys-Saint Vulbas 2 [OPP] [FR] | Outage | 11
FR | N Situation / [IT-IT] Rondissone-Trino [DIR][IT] | N Situation / [IT-IT] Rondissone-Trino [DIR][IT] | Outage | 4
FR | N-2 Albertville-Rondissone / [IT-IT] Casanova-Piossasco [OPP][IT] | N-2 Albertville-Rondissone / [IT-IT] Casanova-Piossasco [OPP][IT] | Outage | 1
FR | Cancellation planned outage Chaffard G.Ile 2 | Cancellation planned outage Chaffard G.Ile 2 | Outage | 7
FR | N-2 Albertville-Rondissone / [IT-IT] Rosone-Villa [OPP][IT] | N-2 Albertville-Rondissone / [IT-IT] Rosone-Villa [OPP][IT] | Outage | 6
FR | N-1 Albertville-Rondissone 1 / [FR-IT] Albertville-Rondissone 2 [OPP] [FR] | N-1 Albertville-Rondissone 1 / [FR-IT] Albertville-Rondissone 2 [OPP] [FR] | Outage | 4
FR | Planned outage of Piossasco-Grande-Ile 1 HVDC | Planned outage of Piossasco-Grande-Ile 1 HVDC | Outage | 2
IT | Allocation Constraint value not properly processed by Coreso | Allocation Constraint value not properly processed by Coreso | Process Fail | 5
IT | Foreseen violations on the border | Foreseen violations on the border | Outage | 27
SI | Overload: CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano, Global TTC reduction tirggered | CNEC: CNE: 400 kV Divaca-Redipuglia, C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 239 | CNE: 400 kV Divaca-Redipuglia, | -2 Robbia-Gorlago + Robbia-S.Fiorano
Smoothing | Smoothing ramp | Smoothing ramp | Smoothing | 51

## ID Full Results Data 2025Q2 (hidden)
ID results
|  |  | TTC Adjustment |  |  | TTC Validated |  |  | ANTC |  |  | LimitedBy | [8 empty] | AT | AT | AT | AT | AT | AT | CH | CH | CH | CH | CH | CH | FR | FR | FR | FR | FR | FR | SI | SI | SI | SI | SI | SI | IT | IT | IT | IT | IT | IT
Business day | Month | Timestamp | TTC_Full_Import | TTCImport | TTCExport | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | 70% red | TTCRed_Import | TTCRed_Transit_Import | TTCRed_Transit_Export | TTRed_Transit | TTC and 70% red | FLAG | Bilateral - MNII | MNII | Reason | Bilateral - MIEC | MNIE | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason | Bilateral | MNII | Reason | Bilateral - MIEC | MIEC | Reason
2025-04-01 | April | 1230 | 8782 |  |  | 8782 |  |  | -2379 | -2379 | -2378 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1330 | 8782 |  |  | 8782 |  |  | -2379 | -2379 | -2378 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1430 | 8782 |  |  | 8782 |  |  | -2379 | -2379 | -2378 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1530 | 8606 |  |  | 8606 |  |  | -1796 | -1796 | -1782 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1630 | 8606 |  |  | 8606 |  |  | -1796 | -1796 | -1782 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1730 | 8606 |  |  | 8606 |  |  | -1796 | -1796 | -1782 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1830 |  | 6460 | 942 |  | 6861 | 951 | 1026 | 10 | 1026 | Minimum Margin | ID schedules | 1016 | NA | -401 | -9 | -410 | 10 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 1930 |  | 7623 | 1071 |  | 7623 | 1071 | -954 | -954 | -954 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 2030 |  | 6996 | 1072 |  | 7253 | 1058 | 614 | 10 | 614 | Minimum Margin | ID schedules | 604 | NA | -257 | 14 | -243 | 10 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-01 | April | 2130 | 9316 |  |  | 9305 |  |  | -1928 | -1928 | -1916 | Critical Branch | Validation phase | 0 | 11 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 9055 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 2230 | 9316 |  |  | 9140 |  |  | -1928 | -1928 | -1752 | Critical Branch | Validation phase | 0 | 176 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 8890 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-01 | April | 2330 | 8506 |  |  | 8506 |  |  | -1075 | -1075 | -1075 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1230 | 8418 |  |  | 8418 |  |  | 0 | 0 | -439 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1330 | 8418 |  |  | 8418 |  |  | 0 | 0 | -439 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1430 | 8494 |  |  | 8494 |  |  | 0 | 0 | -529 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1530 | 8828 |  |  | 8828 |  |  | -446 | -446 | -418 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1630 | 8828 |  |  | 8828 |  |  | -446 | -446 | -418 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1730 | 8828 |  |  | 8828 |  |  | -446 | -446 | -418 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1830 | 7837 |  |  | 7837 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 1930 | 8507 |  |  | 8589 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -82 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 2030 | 8807 |  |  | 8807 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 2130 | 9506 |  |  | 9499 |  |  | -3222 | -3222 | -3214 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 2230 | 9506 |  |  | 9499 |  |  | -3222 | -3222 | -3216 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-02 | April | 2330 | 8696 |  |  | 8688 |  |  | -2502 | -2502 | -2495 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 8 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-03 | April | 1230 | 8118 |  |  | 8118 |  |  | -2985 | -2985 | -2987 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-03 | April | 1330 | 8118 |  |  | 8118 |  |  | -2985 | -2985 | -2987 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-03 | April | 1430 | 8075 |  |  | 8062 |  |  | -2942 | -2942 | -2931 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 13 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-03 | April | 1530 | 8228 |  |  | 8206 |  |  | -4670 | -4670 | -4653 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 22 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-03 | April | 1630 | 8228 |  |  | 8030 |  |  | -4670 | -4670 | -4474 | Critical Branch | Validation phase | 0 | 198 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | 7791 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-03 | April | 1730 | 9528 |  |  | 7997 |  |  | -6026 | -6026 | -4498 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1531 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 8274 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | 3000 | None | Planned outage of Creys-Saint-Vulbas 2 + Praz-Villarodin | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-03 | April | 1830 |  | 5962 | 572 |  | 6059 | 572 | -4077 | -4077 | -4077 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -97 | 0 | -97 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-03 | April | 1930 |  | 6061 | 572 |  | 6061 | 572 | -4592 | -4592 | -4592 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-03 | April | 2030 |  | 5223 | 563 |  | 5479 | 563 | -3602 | -3602 | -3602 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -256 | 0 | -256 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-03 | April | 2130 | 8480 |  |  | 7584 |  |  | -2596 | -2596 | -1706 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 896 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-03 | April | 2230 | 8480 |  |  | 8478 |  |  | -2596 | -2596 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-03 | April | 2330 | 7670 |  |  | 7670 |  |  | -1782 | -1782 | -1782 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 1230 | 8116 |  |  | 8116 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-04 | April | 1330 | 8116 |  |  | 8116 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-04 | April | 1430 | 8116 |  |  | 8116 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-04 | April | 1530 | 7243 |  |  | 7243 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-04 | April | 1630 | 7243 |  |  | 7243 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 1730 | 7442 |  |  | 7442 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 1830 | 6718 |  |  | 6722 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -4 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 1930 | 5301 |  |  | 5301 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 2030 | 6600 |  |  | 6610 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -10 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 2130 | 7061 |  |  | 7074 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -13 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 2230 | 7559 |  |  | 7560 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-04 | April | 2330 | 6938 |  |  | 6938 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-05 | April | 1230 |  | 2595 | 1234 |  | 2189 | 1137 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 406 | 97 | 503 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-05 | April | 1330 |  | 2595 | 1234 |  | 1410 | 1140 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1185 | 94 | 1279 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-05 | April | 1430 |  | 2595 | 1234 |  | 496 | 1202 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2099 | 32 | 2131 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-05 | April | 1530 |  | 2163 | 701 |  | 2438 | 701 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -275 | 0 | -275 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-05 | April | 1630 |  | 3986 | 701 |  | 3949 | 701 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 37 | 0 | 37 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-05 | April | 1730 |  | 4982 | 701 |  | 4982 | 701 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-05 | April | 1830 | 9112 |  |  | 6742 |  |  | 0 | 0 | -643 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 2370 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-05 | April | 1930 | 9112 |  |  | 7556 |  |  | 0 | 0 | -1239 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1556 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-05 | April | 2030 | 9112 |  |  | 8644 |  |  | 0 | 0 | -2178 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 468 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-05 | April | 2130 | 9873 |  |  | 9236 |  |  | 0 | 0 | -1418 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 637 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-05 | April | 2230 | 9873 |  |  | 9236 |  |  | 0 | 0 | -1418 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 637 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-05 | April | 2330 | 9063 |  |  | 8571 |  |  | 0 | 0 | -684 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 492 | NA | NA | NA | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 435 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-06 | April | 1230 |  | 2642 | 718 |  | 2772 | 718 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -130 | 0 | -130 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-06 | April | 1330 |  | 2772 | 718 |  | 2772 | 718 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-06 | April | 1430 |  | 2642 | 718 |  | 2772 | 718 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -130 | 0 | -130 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-06 | April | 1530 |  | 2342 | 418 |  | 2496 | 418 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -154 | 0 | -154 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-06 | April | 1630 |  | 2804 | 418 |  | 2804 | 418 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-06 | April | 1730 |  | 2342 | 418 |  | 2496 | 418 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -154 | 0 | -154 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-06 | April | 1830 |  | 4236 | 914 |  | 4236 | 914 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-06 | April | 1930 |  | 5475 | 892 |  | 5475 | 903 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -11 | -11 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-06 | April | 2030 |  | 6021 | 812 |  | 6021 | 893 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -81 | -81 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-06 | April | 2130 |  | 6280 | 597 |  | 6280 | 597 | 4045 | 0 | 4045 | Critical Branch | ID schedules | 4045 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-06 | April | 2230 |  | 6010 | 718 |  | 6010 | 718 | 4227 | 0 | 4227 | ID schedules | ID schedules | 4227 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-06 | April | 2330 |  | 6132 | 718 |  | 6132 | 718 | 4090 | 0 | 4090 | ID schedules | ID schedules | 4090 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-07 | April | 1230 | 6449 |  |  | 6449 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1330 | 6449 |  |  | 6449 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1430 | 6449 |  |  | 6449 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1530 |  | 6404 | -93 |  | 6404 | -90 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -3 | -3 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1630 |  | 6523 | 703 |  | 6523 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1730 |  | 5900 | 703 |  | 5900 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1830 |  | 5488 | 877 |  | 5947 | 933 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | -459 | -56 | -515 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 1930 |  | 5844 | 935 |  | 5011 | 935 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 833 | 0 | 833 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 4289 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 2030 |  | 5488 | 877 |  | 4671 | 909 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 817 | -32 | 785 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 4078 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 2130 |  | 5620 | 830 |  | 6142 | 830 | 41 | 0 | 41 | ID schedules | Smoothing ramp | 41 | NA | -522 | 0 | -522 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 2230 |  | 7397 | 830 |  | 7397 | 830 | -1893 | -1893 | -1893 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-07 | April | 2330 |  | 5839 | 692 |  | 6083 | 691 | -430 | -430 | -430 | Critical Branch | ID schedules | 0 | NA | -244 | 1 | -243 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-08 | April | 1230 |  | 6805 | 130 |  | 6809 | 130 | 15080 | -72 | 15080 | ID schedules | ID schedules | 15152 | NA | -4 | 0 | -4 | -72 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 6614 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 1330 |  | 6570 | 72 |  | 6552 | 72 | 15247 | -72 | 15247 | ID schedules | ID schedules | 15319 | NA | 18 | 0 | 18 | -72 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 6379 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 1430 |  | 6678 | 130 |  | 6678 | 130 | 15083 | -72 | 15083 | ID schedules | ID schedules | 15155 | NA | 0 | 0 | 0 | -72 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 6487 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 1530 | 6414 |  |  | 6414 |  |  | 14450 | -27 | 13370 | ID schedules | ID schedules | 14477 | 0 | NA | NA | NA | -1107 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-08 | April | 1630 | 7160 |  |  | 7160 |  |  | 13704 | -27 | 13076 | ID schedules | ID schedules | 13731 | 0 | NA | NA | NA | -655 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-08 | April | 1730 | 6028 |  |  | 6056 |  |  | 14836 | -27 | 13221 | ID schedules | ID schedules | 14863 | -28 | NA | NA | NA | -1642 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-08 | April | 1830 |  | 4883 | 792 |  | 5516 | 792 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -633 | 0 | -633 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 1930 |  | 5684 | 684 |  | 5186 | 677 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 498 | 7 | 505 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 4645 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | 3200 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 2030 |  | 4002 | 795 |  | 4755 | 795 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -753 | 0 | -753 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 4308 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 2130 |  | 6042 | 803 |  | 6299 | 803 | -1107 | -1107 | -1107 | ID schedules | Smoothing ramp | 0 | NA | -257 | 0 | -257 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 2230 |  | 6732 | 860 |  | 6732 | 860 | -1999 | -1999 | -1999 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-08 | April | 2330 |  | 6480 | 879 |  | 6481 | 889 | -1974 | -1974 | -1974 | Critical Branch | ID schedules | 0 | NA | -1 | -10 | -11 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-09 | April | 1230 | 7449 |  |  | 7449 |  |  | -1917 | -1917 | -1837 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 1330 | 7449 |  |  | 7449 |  |  | -1917 | -1917 | -1837 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 1430 | 7449 |  |  | 7449 |  |  | -1917 | -1917 | -1837 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 1530 | 8375 |  |  | 8375 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 1630 | 8366 |  |  | 8366 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 1730 | 7876 |  |  | 7876 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 1830 |  | 6622 | 867 |  | 6725 | 880 | -1755 | -1755 | -1755 | Critical Branch | ID schedules | 0 | NA | -103 | -13 | -116 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-09 | April | 1930 |  | 7407 | 777 |  | 7407 | 777 | -2374 | -2374 | -2374 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 2030 |  | 7272 | 867 |  | 7306 | 879 | -2206 | -2206 | -2206 | ID schedules | ID schedules | 0 | NA | -34 | -12 | -46 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 7071 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 2130 |  | 7615 | 702 |  | 7931 | 702 | -1391 | -1391 | -1391 | ID schedules | ID schedules | 0 | NA | -316 | 0 | -316 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 2230 |  | 7890 | 702 |  | 7960 | 702 | -2516 | -2516 | -2516 | ID schedules | ID schedules | 0 | NA | -70 | 0 | -70 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-09 | April | 2330 |  | 7174 | 720 |  | 7447 | 720 | -1034 | -1034 | -1034 | ID schedules | ID schedules | 0 | NA | -273 | 0 | -273 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-10 | April | 1230 | 7786 |  |  | 7786 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 1330 | 7786 |  |  | 7786 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 1430 | 7786 |  |  | 7786 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 1530 | 7038 |  |  | 7038 |  |  | 14967 | -45 | 14966 | ID schedules | TTC Validation phase - bilateral reduction | 15012 | 0 | NA | NA | NA | -46 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 1630 | 7038 |  |  | 7038 |  |  | 14967 | -45 | 14966 | ID schedules | TTC Validation phase - bilateral reduction | 15012 | 0 | NA | NA | NA | -46 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 1730 | 7038 |  |  | 7038 |  |  | 14967 | -45 | 14966 | ID schedules | TTC Validation phase - bilateral reduction | 15012 | 0 | NA | NA | NA | -46 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 1830 |  | 7263 | 875 |  | 7263 | 558 | 12410 | -81 | 12410 | ID schedules | Smoothing ramp | 12491 | NA | 0 | 317 | 317 | -81 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2600 | None | Planned outage of Creys-Saint-Vulbas 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-10 | April | 1930 |  | 7125 | 883 |  | 7125 | 883 | 12486 | -81 | 12486 | ID schedules | Smoothing ramp | 12567 | NA | 0 | 0 | 0 | -81 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 6872 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-10 | April | 2030 |  | 7304 | 883 |  | 7317 | 883 | 12704 | -81 | 12704 | ID schedules | Smoothing ramp | 12785 | NA | -13 | 0 | -13 | -81 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-10 | April | 2130 | 7477 |  |  | 7477 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-10 | April | 2230 | 7458 |  |  | 7458 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-10 | April | 2330 | 6656 |  |  | 6656 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-11 | April | 1230 | 6288 |  |  | 6288 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-11 | April | 1330 | 6288 |  |  | 6288 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-11 | April | 1430 | 6288 |  |  | 6288 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-11 | April | 1530 | 5226 |  |  | 5226 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-11 | April | 1630 | 6500 |  |  | 6500 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-11 | April | 1730 | 7888 |  |  | 7888 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-11 | April | 1830 |  | 7547 | 489 |  | 7547 | 484 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 5 | 5 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-11 | April | 1930 |  | 7458 | 492 |  | 7458 | 492 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-11 | April | 2030 |  | 7570 | 496 |  | 7570 | 496 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-11 | April | 2130 |  | 7497 | 699 |  | 7497 | 699 | -2615 | -2615 | -2615 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-11 | April | 2230 |  | 7387 | 699 |  | 7387 | 698 | -2560 | -2560 | -2560 | ID schedules | ID schedules | 0 | NA | 0 | 1 | 1 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-11 | April | 2330 |  | 6874 | 684 |  | 6874 | 677 | -2093 | -2093 | -2093 | ID schedules | ID schedules | 0 | NA | 0 | 7 | 7 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 1230 | 4130 |  |  | 4267 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -137 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-12 | April | 1330 | 3123 |  |  | 3283 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -160 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-12 | April | 1430 | 3165 |  |  | 3386 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -221 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-12 | April | 1530 |  | 7430 | 815 |  | 4456 | 815 | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | NA | 2974 | 0 | 2974 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-12 | April | 1630 |  | 6540 | 877 |  | 6447 | 877 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 93 | 0 | 93 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 43 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-12 | April | 1730 |  | 7430 | 815 |  | 6463 | 139 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 967 | 676 | 1643 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 1830 |  | 7148 | 877 |  | 7148 | 877 | -2138 | -2138 | -2138 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 1930 |  | 7243 | 877 |  | 7243 | 877 | -2456 | -2456 | -2456 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 2030 |  | 7276 | 877 |  | 7276 | 877 | -2054 | -2054 | -2054 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 2130 |  | 7791 | 699 |  | 7791 | 689 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 10 | 10 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 2230 |  | 7791 | 549 |  | 7791 | 534 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 15 | 15 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-12 | April | 2330 |  | 7085 | -474 |  | 7085 | -474 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1230 | 6765 |  |  | 6765 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1330 | 6765 |  |  | 6765 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1430 | 6765 |  |  | 6765 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1530 |  | 6980 | 889 |  | 6474 | 800 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 506 | 89 | 595 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1630 |  | 7280 | 889 |  | 7039 | 732 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 241 | 157 | 398 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1730 |  | 7280 | 889 |  | 7029 | 380 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 251 | 509 | 760 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1830 |  | 6662 | 60 |  | 6662 | 60 | -3033 | -3033 | -3033 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 1930 |  | 7185 | 815 |  | 7185 | 815 | -2529 | -2529 | -2529 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 2030 |  | 6741 | 753 |  | 6741 | 775 | -2563 | -2563 | -2563 | ID schedules | ID schedules | 0 | NA | 0 | -22 | -22 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 2130 | 7284 |  |  | 7289 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -5 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 2230 | 7069 |  |  | 7069 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-13 | April | 2330 | 6691 |  |  | 6697 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -6 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1230 | 5734 |  |  | 5734 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1330 | 5734 |  |  | 5734 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1430 | 5734 |  |  | 5734 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1530 | 6621 |  |  | 6621 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1630 | 6598 |  |  | 6598 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1730 | 6308 |  |  | 6308 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1830 |  | 4234 | 881 |  | 4470 | 881 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -236 | 0 | -236 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 1930 |  | 4237 | 881 |  | 3855 | 881 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 382 | 0 | 382 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | 3435 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-14 | April | 2030 |  | 3170 | 881 |  | 3689 | 881 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -519 | 0 | -519 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-14 | April | 2130 | 5725 |  |  | 5725 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 2230 | 6458 |  |  | 6458 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-14 | April | 2330 | 6176 |  |  | 6176 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 1230 | 7181 |  |  | 7181 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 1330 | 7130 |  |  | 7130 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 1430 | 7239 |  |  | 7239 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 1530 | 7142 |  |  | 7142 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 1630 | 6952 |  |  | 6951 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-15 | April | 1730 | 7165 |  |  | 7165 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-15 | April | 1830 |  | 6570 | 391 |  | 6570 | 421 | -2504 | -2504 | -2504 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -30 | -30 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-15 | April | 1930 |  | 6637 | 881 |  | 6637 | 881 | -1638 | -1638 | -1638 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 2030 |  | 6622 | 856 |  | 6622 | 876 | -1923 | -1923 | -1923 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -20 | -20 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 2130 | 7314 |  |  | 7309 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 5 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 2230 | 7489 |  |  | 7489 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-15 | April | 2330 | 7154 |  |  | 7154 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2000 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 1230 | 7248 |  |  | 7248 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-16 | April | 1330 | 7248 |  |  | 7248 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-16 | April | 1430 | 7248 |  |  | 7248 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-16 | April | 1530 | 7247 |  |  | 7247 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-16 | April | 1630 | 7247 |  |  | 7247 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-16 | April | 1730 | 7241 |  |  | 7241 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 1830 |  | 5727 | 701 |  | 5727 | 701 | 27977 | 0 | 27977 | Critical Branch | TTC Validation phase - bilateral reduction | 27977 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 1930 |  | 6698 | 701 |  | 6177 | 701 | 26649 | 0 | 26649 | Critical Branch | TTC Validation phase - bilateral reduction | 26649 | NA | 521 | 0 | 521 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 2030 |  | 4717 | 701 |  | 4717 | 701 | 28443 | 0 | 28443 | Critical Branch | TTC Validation phase - bilateral reduction | 28443 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 2130 | 6728 |  |  | 6728 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 2230 | 7451 |  |  | 7451 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-16 | April | 2330 | 7084 |  |  | 7084 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 2200 | None | N-1 CHAFFARD-G.ILE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-17 | April | 1230 | 6210 |  |  | 6210 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-17 | April | 1330 | 6210 |  |  | 6210 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-17 | April | 1430 | 6210 |  |  | 6210 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-17 | April | 1530 | 7380 |  |  | 7380 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-17 | April | 1630 | 7430 |  |  | 7430 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-17 | April | 1730 | 7021 |  |  | 7021 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-17 | April | 1830 | 6958 |  |  | 6958 |  |  | 0 | 0 | 9697 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 9697 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-17 | April | 1930 | 6980 |  |  | 6980 |  |  | 0 | 0 | 9696 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 9696 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-17 | April | 2030 | 6981 |  |  | 6981 |  |  | 0 | 0 | 9696 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 9696 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-17 | April | 2130 | 6960 |  |  | 6960 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-17 | April | 2230 | 6960 |  |  | 6960 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-17 | April | 2330 | 6342 |  |  | 6342 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-18 | April | 1230 | 4235 |  |  | 4235 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1330 | 5259 |  |  | 5259 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1430 | 5361 |  |  | 5361 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1530 | 5564 |  |  | 5564 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1630 | 4514 |  |  | 4514 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1730 | 5563 |  |  | 5563 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1830 | 8675 |  |  | 8225 |  |  | -4548 | -4548 | -4163 | Critical Branch | Smoothing ramp | 0 | 450 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 1930 | 8675 |  |  | 8563 |  |  | -4548 | -4548 | -4438 | Critical Branch | Smoothing ramp | 0 | 112 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 2030 | 8675 |  |  | 8675 |  |  | -4548 | -4548 | -4547 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 2130 | 8984 |  |  | 8984 |  |  | 0 | 0 | -2159 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 2230 | 8984 |  |  | 8984 |  |  | 0 | 0 | -2159 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-18 | April | 2330 | 8174 |  |  | 8174 |  |  | 0 | 0 | -1321 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1230 | 4493 |  |  | 4467 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 214 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1330 | 4493 |  |  | 4467 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 214 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1430 | 4493 |  |  | 4467 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 26 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 214 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1530 | 5349 |  |  | 5288 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 61 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 214 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1630 | 5349 |  |  | 5288 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 61 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 214 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1730 | 5349 |  |  | 5288 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 61 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 214 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-19 | April | 1830 | 5515 |  |  | 5515 |  |  | -1604 | -1604 | -1604 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-19 | April | 1930 | 5515 |  |  | 5515 |  |  | -1604 | -1604 | -1604 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-19 | April | 2030 | 5515 |  |  | 5514 |  |  | -1604 | -1604 | -2232 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-19 | April | 2130 |  | 7125 | 876 |  | 7125 | 876 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-19 | April | 2230 |  | 7642 | 876 |  | 7642 | 876 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-19 | April | 2330 |  | 7191 | 790 |  | 7191 | 796 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -6 | -6 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-20 | April | 1230 |  | 3778 | 3113 |  | 584 | 2429 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3194 | 684 | 3878 | 0 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 1330 |  | 3778 | 3113 |  | 584 | 1553 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3194 | 1560 | 4754 | 0 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 1430 |  | 3778 | 3113 |  | 584 | 677 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3194 | 2436 | 5630 | 0 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 1530 |  | 3278 | 2874 |  | 508 | 479 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2770 | 2395 | 5165 | 0 | 1 | 148 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 1630 |  | 3278 | 2874 |  | 482 | 460 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2796 | 2414 | 5210 | 0 | 1 | 148 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 1730 |  | 3278 | 2874 |  | -320 | -1312 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3598 | 4186 | 7784 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 1830 | 6044 |  |  | 3423 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 2621 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 199 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-20 | April | 1930 | 6044 |  |  | 4794 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1250 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 68 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-20 | April | 2030 | 6044 |  |  | 5626 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 418 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-20 | April | 2130 |  | 5262 | 907 |  | 5260 | 907 | -1266 | -1266 | -1266 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 2 | 0 | 2 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 2230 |  | 5264 | 907 |  | 5264 | 907 | -1286 | -1286 | -1286 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-20 | April | 2330 |  | 5250 | 831 |  | 5250 | 831 | -1290 | -1290 | -1290 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 94 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -94 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-21 | April | 1230 |  | 3278 | 2874 |  | 1443 | 2612 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1835 | 262 | 2097 | 0 | 1 | 148 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-21 | April | 1330 |  | 3278 | 2874 |  | 1442 | 2608 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1836 | 266 | 2102 | 0 | 1 | 148 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-21 | April | 1430 |  | 3278 | 2874 |  | 1443 | 2609 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1835 | 265 | 2100 | 0 | 1 | 148 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-21 | April | 1530 |  | -566 | 2522 |  | -566 | 2441 | 7645 | 0 | 7645 | Critical Branch | TTC Validation phase - bilateral reduction | 7645 | NA | 0 | 81 | 81 | 0 | 1 | 147 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-21 | April | 1630 |  | 1089 | 2696 |  | 1089 | 2792 | 6244 | 0 | 6244 | Critical Branch | TTC Validation phase - bilateral reduction | 6244 | NA | 0 | -96 | -96 | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-21 | April | 1730 |  | 1089 | 2728 |  | 1089 | 2815 | 6270 | 0 | 6270 | Critical Branch | TTC Validation phase - bilateral reduction | 6270 | NA | 0 | -87 | -87 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-21 | April | 1830 |  | 6376 | 1217 |  | 2907 | 1217 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3469 | 0 | 3469 | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | -170 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-21 | April | 1930 |  | 6376 | 1217 |  | 4443 | 907 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1933 | 310 | 2243 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-21 | April | 2030 |  | 6376 | 1217 |  | 5559 | 907 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 817 | 310 | 1127 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-21 | April | 2130 |  | 4910 | 880 |  | 5344 | 881 | -3331 | -3331 | -3331 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -434 | -1 | -435 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-21 | April | 2230 |  | 5025 | 847 |  | 5254 | 858 | -3478 | -3478 | -3478 | ID schedules | ID schedules | 0 | NA | -229 | -11 | -240 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-21 | April | 2330 |  | 5059 | 907 |  | 5280 | 907 | -3014 | -3014 | -3014 | ID schedules | ID schedules | 0 | NA | -221 | 0 | -221 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-22 | April | 1230 | 2561 |  |  | 2561 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-22 | April | 1330 | 2877 |  |  | 2877 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-22 | April | 1430 | 4266 |  |  | 4266 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-22 | April | 1530 | 4427 |  |  | 4427 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-22 | April | 1630 | 4953 |  |  | 4953 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1600 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-22 | April | 1730 | 4978 |  |  | 4978 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1600 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-22 | April | 1830 | 4151 |  |  | 4151 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-22 | April | 1930 | 2687 |  |  | 2687 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-22 | April | 2030 | 2560 |  |  | 2560 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-22 | April | 2130 |  | 3314 | 703 |  | 3318 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -4 | 0 | -4 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-22 | April | 2230 |  | 3969 | 703 |  | 3961 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 8 | 0 | 8 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-22 | April | 2330 |  | 3837 | 720 |  | 3837 | 720 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-23 | April | 1230 | 4140 |  |  | 4140 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 1330 | 4169 |  |  | 4169 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 1430 | 4178 |  |  | 4178 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 1530 | 4172 |  |  | 4172 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 1630 | 3996 |  |  | 3996 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 1730 | 4589 |  |  | 4618 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -29 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-23 | April | 1830 |  | 3742 | 703 |  | 3742 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-23 | April | 1930 |  | 3126 | 703 |  | 3126 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-23 | April | 2030 |  | 3608 | 703 |  | 3608 | 703 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-23 | April | 2130 | 3546 |  |  | 3546 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 2230 | 4169 |  |  | 4169 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-23 | April | 2330 | 3958 |  |  | 3958 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1230 | 1536 |  |  | 1536 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 135 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1330 | 1532 |  |  | 1507 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 25 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1430 | 1858 |  |  | 1851 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 7 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1530 | 2366 |  |  | 2366 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 243 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1630 | 2955 |  |  | 2955 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 174 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1730 | 2673 |  |  | 2673 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 182 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1830 | 3303 |  |  | 3322 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -19 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 1930 | 3983 |  |  | 3983 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 2030 | 3334 |  |  | 3334 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 2130 | 4018 |  |  | 4018 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 375 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 2230 | 3973 |  |  | 3973 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 448 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-24 | April | 2330 | 3965 |  |  | 3965 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1230 | -2626 |  |  | -2626 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1330 | -1416 |  |  | -1416 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1430 | -1390 |  |  | -1390 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1530 | -1410 |  |  | -1410 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1630 | -955 |  |  | -955 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1730 | 762 |  |  | 2070 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -1308 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1830 | 3278 |  |  | 3646 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -368 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 1930 | 4646 |  |  | 4826 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -180 | NA | NA | NA | 0 | 1 | 173 | None | Reduction because NTC over thermal limit on border | 41 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 2030 | 5842 |  |  | 5886 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -44 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 2130 | 6700 |  |  | 6700 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 74 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 2230 | 6375 |  |  | 6375 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 236 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-25 | April | 2330 | 6825 |  |  | 6825 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 215 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 490 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-26 | April | 1230 |  | 1580 | 515 |  | 1692 | 671 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -112 | -156 | -268 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-26 | April | 1330 |  | 1643 | 450 |  | 1595 | 576 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 48 | -126 | -78 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-26 | April | 1430 |  | 1728 | 450 |  | 1317 | 418 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 411 | 32 | 443 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-26 | April | 1530 |  | 2003 | 618 |  | 1500 | 585 | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | NA | 503 | 33 | 536 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-26 | April | 1630 |  | 2048 | 684 |  | 2048 | 688 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -4 | -4 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-26 | April | 1730 |  | 2003 | 618 |  | 1579 | 618 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 424 | 0 | 424 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-26 | April | 1830 |  | 4468 | 892 |  | 4468 | 892 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-26 | April | 1930 |  | 5968 | 892 |  | 5968 | 892 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-26 | April | 2030 |  | 7412 | 837 |  | 7412 | 837 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-26 | April | 2130 | 8190 |  |  | 8204 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | -14 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-26 | April | 2230 | 9116 |  |  | 9103 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 13 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7848 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 RONDISSONE-TRINO | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-26 | April | 2330 | 8810 |  |  | 8815 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -5 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-27 | April | 1230 | 2732 |  |  | 2732 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-27 | April | 1330 | 2732 |  |  | 2732 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-27 | April | 1430 | 2732 |  |  | 2732 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-27 | April | 1530 | 2940 |  |  | 2940 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 435 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-27 | April | 1630 | 3168 |  |  | 3168 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-27 | April | 1730 | 4113 |  |  | 4113 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 170 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-27 | April | 1830 |  | 5930 | 910 |  | 5930 | 910 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-27 | April | 1930 |  | 6432 | 454 |  | 6432 | 454 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-27 | April | 2030 |  | 6462 | 547 |  | 6462 | 549 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -2 | -2 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-27 | April | 2130 | 7531 |  |  | 7531 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-27 | April | 2230 | 7539 |  |  | 7539 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-27 | April | 2330 | 7286 |  |  | 7286 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-28 | April | 1230 | 7481 |  |  | 7446 |  |  | -3362 | -3362 | -3330 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 35 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1330 | 7481 |  |  | 7446 |  |  | -3362 | -3362 | -3330 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 35 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1430 | 7481 |  |  | 7446 |  |  | -3362 | -3362 | -3330 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 35 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1530 | 6353 |  |  | 6353 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 419 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1630 | 6253 |  |  | 6253 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 417 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1730 | 7685 |  |  | 7685 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 421 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1830 | 8277 |  |  | 8282 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -5 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 450 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 1930 | 5523 |  |  | 5523 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | -155 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 2030 | 5132 |  |  | 5132 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | -155 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-28 | April | 2130 |  | 5866 | 852 |  | 5868 | 852 | -1945 | -1945 | -1945 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -2 | 0 | -2 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-28 | April | 2230 |  | 6201 | 877 |  | 6201 | 877 | -2392 | -2392 | -2392 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-28 | April | 2330 |  | 6074 | 925 |  | 6074 | 323 | -2585 | -2585 | -2585 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 602 | 602 | 0 | 1 | 170 | None | Reduction because NTC over thermal limit on border | 417 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-29 | April | 1230 | 7383 |  |  | 7338 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 45 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 329 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-29 | April | 1330 | 7383 |  |  | 7338 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 45 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 329 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-29 | April | 1430 | 7383 |  |  | 7338 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 45 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 329 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-29 | April | 1530 | 7060 |  |  | 7056 |  |  | -1777 | -1777 | -1773 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 4 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 357 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-29 | April | 1630 | 7060 |  |  | 7056 |  |  | -1777 | -1777 | -1773 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 4 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 357 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-29 | April | 1730 | 7060 |  |  | 7056 |  |  | -1777 | -1777 | -1773 | Critical Branch | Critical Branch | 0 | 4 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 219 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-29 | April | 1830 |  | 6924 | 176 |  | 6924 | 176 | -1239 | -1239 | -1239 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-29 | April | 1930 |  | 6643 | 462 |  | 6198 | 249 | -1172 | -1172 | -1172 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 445 | 213 | 658 | 0 | 1 | 155 | None | Reduction because NTC over thermal limit on border | 109 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-29 | April | 2030 |  | 3914 | 473 |  | 4307 | 257 | 585 | 11 | 585 | Minimum Margin | TTC Validation phase - bilateral reduction | 574 | NA | -393 | 216 | -177 | 11 | 1 | 155 | None | Reduction because NTC over thermal limit on border | -153 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | 1378 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-29 | April | 2130 |  | 4840 | 190 |  | 5197 | 176 | 2094 | 2 | 2094 | Minimum Margin | TTC Validation phase - bilateral reduction | 2092 | NA | -357 | 14 | -343 | 2 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1754 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-29 | April | 2230 |  | 8503 | 176 |  | 6800 | 176 | -2082 | -2082 | -2082 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 1703 | 0 | 1703 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-29 | April | 2330 |  | 5554 | 194 |  | 5793 | 105 | 1140 | 2 | 1140 | Minimum Margin | TTC Validation phase - bilateral reduction | 1138 | NA | -239 | 89 | -150 | 2 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2157 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-04-30 | April | 1230 | 5203 |  |  | 5203 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 379 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1330 | 5203 |  |  | 5203 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 379 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1430 | 5203 |  |  | 5203 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 379 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1530 | 6293 |  |  | 5965 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 328 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1630 | 6293 |  |  | 5946 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 347 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1730 | 7193 |  |  | 7049 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 144 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 8 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1830 | 6751 |  |  | 6751 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 1930 | 5620 |  |  | 5620 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-04-30 | April | 2030 | 4419 |  |  | 4419 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-30 | April | 2130 |  | 5525 | 873 |  | 5653 | 873 | -1462 | -1462 | -1462 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -128 | 0 | -128 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-30 | April | 2230 |  | 7745 | 873 |  | 6964 | 873 | -4348 | -4348 | -4348 | ID schedules | Smoothing ramp | 0 | NA | 781 | 0 | 781 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-04-30 | April | 2330 |  | 6439 | 676 |  | 6662 | 735 | -2552 | -2552 | -2552 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -223 | -59 | -282 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-01 | May | 1230 |  | 1136 | 915 |  | 956 | 862 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 180 | 53 | 233 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1330 |  | 1136 | 915 |  | 956 | 862 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 180 | 53 | 233 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1430 |  | 1136 | 915 |  | -45 | 904 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1181 | 11 | 1192 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1530 |  | 1925 | 645 |  | 819 | 645 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1106 | 0 | 1106 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 49 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1630 |  | 1158 | 678 |  | 1146 | 678 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 12 | 0 | 12 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1730 |  | 2143 | 678 |  | 2143 | 678 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1830 |  | 7263 | 864 |  | 3924 | 711 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 3339 | 153 | 3492 | 0 | 1 | 130 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -114 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 1930 |  | 7263 | 864 |  | 4833 | 639 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2430 | 225 | 2655 | 0 | 1 | 115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -115 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 2030 |  | 7263 | 864 |  | 5633 | 644 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1630 | 220 | 1850 | 0 | 1 | 116 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -116 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 2130 |  | 5537 | 901 |  | 5883 | 901 | -593 | -593 | -593 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -346 | 0 | -346 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -42 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 2230 |  | 6027 | 910 |  | 6307 | 910 | -1168 | -1168 | -1168 | ID schedules | ID schedules | 0 | NA | -280 | 0 | -280 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -10 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-01 | May | 2330 |  | 4675 | 532 |  | 5146 | 596 | -59 | -59 | -59 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -471 | -64 | -535 | 0 | 1 | 158 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -131 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-02 | May | 1230 | 2505 |  |  | 2505 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-02 | May | 1330 | 2512 |  |  | 2512 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-02 | May | 1430 | 2602 |  |  | 2602 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-02 | May | 1530 | 2988 |  |  | 2988 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-02 | May | 1630 | 2828 |  |  | 2828 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-02 | May | 1730 | 3405 |  |  | 3405 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-02 | May | 1830 |  | 6049 | 615 |  | 6281 | 615 | -1826 | -1826 | -1826 | ID schedules | Smoothing ramp | 0 | NA | -232 | 0 | -232 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-02 | May | 1930 |  | 7047 | 614 |  | 6774 | 614 | -2899 | -2899 | -2899 | ID schedules | Smoothing ramp | 0 | NA | 273 | 0 | 273 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-02 | May | 2030 |  | 6576 | 614 |  | 6646 | 614 | -2413 | -2413 | -2413 | ID schedules | ID schedules | 0 | NA | -70 | 0 | -70 | 0 | 1 | None | None | None | None | None | None | None | None | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 158% | None | 5682 | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 158% | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-02 | May | 2130 |  | 7161 | 766 |  | 7237 | 766 | -2260 | -2260 | -2260 | ID schedules | ID schedules | 0 | NA | -76 | 0 | -76 | 0 | 1 | None | None | None | None | None | None | None | None | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 151% | None | 6122 | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 151% | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-02 | May | 2230 |  | 7602 | 766 |  | 7390 | 766 | -2772 | -2772 | -2772 | ID schedules | ID schedules | 0 | NA | 212 | 0 | 212 | 0 | 1 | None | None | None | None | None | None | None | None | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 145% | None | 6279 | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 145% | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-02 | May | 2330 |  | 7420 | 670 |  | 7365 | 710 | -2332 | -2332 | -2332 | ID schedules | ID schedules | 0 | NA | 55 | -40 | 15 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-03 | May | 1230 |  | 638 | 614 |  | 637 | 614 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 47 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-03 | May | 1330 |  | 870 | 516 |  | 362 | 275 | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | NA | 508 | 241 | 749 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 44 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-03 | May | 1430 |  | 635 | 525 |  | 635 | 525 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 146 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-03 | May | 1530 | 963 |  |  | 884 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 79 | NA | NA | NA | 0 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-03 | May | 1630 | 1290 |  |  | 1290 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-03 | May | 1730 | 2200 |  |  | 2200 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-03 | May | 1830 |  | 4361 | 771 |  | 4361 | 771 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-03 | May | 1930 |  | 5861 | 771 |  | 5861 | 771 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-03 | May | 2030 |  | 6650 | 466 |  | 6650 | 424 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 42 | 42 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-03 | May | 2130 |  | 7211 | 282 |  | 7211 | 282 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-03 | May | 2230 |  | 7211 | 289 |  | 7211 | 289 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-03 | May | 2330 |  | 6908 | 130 |  | 6908 | 128 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 2 | 2 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-04 | May | 1230 |  | 552 | 121 |  | 569 | 121 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -17 | 0 | -17 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 81 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-04 | May | 1330 |  | 886 | 97 |  | 870 | 97 | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | NA | 16 | 0 | 16 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 48 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-04 | May | 1430 |  | 946 | 97 |  | 883 | 97 | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 0 | NA | 63 | 0 | 63 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-04 | May | 1530 |  | 550 | 75 |  | 550 | 75 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-04 | May | 1630 |  | 612 | 98 |  | 612 | 98 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-04 | May | 1730 |  | 2191 | 757 |  | 2191 | 757 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-04 | May | 1830 |  | 4287 | 899 |  | 4287 | 899 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-04 | May | 1930 |  | 6552 | 899 |  | 5787 | 899 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 765 | 0 | 765 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-04 | May | 2030 |  | 7173 | 865 |  | 6612 | 452 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 561 | 413 | 974 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-04 | May | 2130 |  | 6901 | 181 |  | 7155 | 181 | -1148 | -1148 | -1148 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -254 | 0 | -254 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-04 | May | 2230 |  | 7043 | 181 |  | 7224 | 181 | -1405 | -1405 | -1405 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -181 | 0 | -181 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-04 | May | 2330 |  | 6247 | 181 |  | 6588 | 181 | -821 | -821 | -821 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -341 | 0 | -341 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 1230 | 5384 |  |  | 5384 |  |  | 12713 | -90 | 12417 | ID schedules | ID schedules | 12803 | 0 | NA | NA | NA | -386 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-05 | May | 1330 | 5377 |  |  | 5377 |  |  | 12720 | -90 | 12417 | ID schedules | ID schedules | 12810 | 0 | NA | NA | NA | -393 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-05 | May | 1430 | 5387 |  |  | 5387 |  |  | 12710 | -90 | 12417 | ID schedules | ID schedules | 12800 | 0 | NA | NA | NA | -383 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-05 | May | 1530 | 5788 |  |  | 5788 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 1630 | 5754 |  |  | 5754 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 1730 | 5784 |  |  | 5784 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 1830 | 6043 |  |  | 6043 |  |  | -3500 | -3500 | -3703 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 1930 | 5773 |  |  | 5773 |  |  | -3230 | -3230 | -3394 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 2030 | 5181 |  |  | 5181 |  |  | -2638 | -2638 | -3118 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 2130 |  | 5360 | -30 |  | 5364 | 2 | 9791 | -14 | 9791 | ID schedules | ID schedules | 9805 | NA | -4 | -32 | -36 | -14 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 2230 |  | 5560 | 708 |  | 5560 | 708 | 9935 | -14 | 9935 | ID schedules | ID schedules | 9949 | NA | 0 | 0 | 0 | -14 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-05 | May | 2330 |  | 5024 | 161 |  | 5024 | 176 | 10226 | -14 | 10226 | ID schedules | ID schedules | 10240 | NA | 0 | -15 | -15 | -14 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1230 | 7280 |  |  | 7280 |  |  | 0 | 0 | -2120 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1330 | 7960 |  |  | 7960 |  |  | 0 | 0 | -2774 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1430 | 7286 |  |  | 7286 |  |  | 0 | 0 | -2093 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1530 |  | 5366 | -153 |  | 5366 | -153 | -1045 | -1045 | -1045 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1630 |  | 5402 | 625 |  | 5402 | 626 | -1094 | -1094 | -1094 | ID schedules | ID schedules | 0 | NA | 0 | -1 | -1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1730 |  | 5427 | 646 |  | 5428 | 560 | -858 | -858 | -858 | ID schedules | ID schedules | 0 | NA | -1 | 86 | 85 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1830 |  | 6330 | 593 |  | 6331 | 593 | -914 | -914 | -914 | ID schedules | ID schedules | 0 | NA | -1 | 0 | -1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 1930 |  | 6121 | 587 |  | 6121 | 587 | -797 | -797 | -797 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 2030 |  | 5738 | 591 |  | 6004 | 591 | -615 | -615 | -615 | ID schedules | ID schedules | 0 | NA | -266 | 0 | -266 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 2130 |  | 6035 | 169 |  | 6306 | 169 | -683 | -683 | -683 | ID schedules | ID schedules | 0 | NA | -271 | 0 | -271 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 2230 |  | 6402 | 169 |  | 6451 | 169 | -933 | -933 | -933 | ID schedules | ID schedules | 0 | NA | -49 | 0 | -49 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-06 | May | 2330 |  | 5869 | 191 |  | 5862 | 191 | -633 | -633 | -633 | ID schedules | ID schedules | 0 | NA | 7 | 0 | 7 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 1230 | 5489 |  |  | 5489 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -262 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 262 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 1330 | 5419 |  |  | 5436 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -17 | NA | NA | NA | 0 | 1 | -262 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 262 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 1430 | 5677 |  |  | 5677 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -262 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 262 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 1530 |  | 5222 | 337 |  | 5222 | 337 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-07 | May | 1630 |  | 5308 | 336 |  | 5308 | 336 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-07 | May | 1730 |  | 5317 | 281 |  | 5317 | 282 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -1 | -1 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-07 | May | 1830 | 5945 |  |  | 5945 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 1930 | 6157 |  |  | 6157 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 2030 | 5781 |  |  | 5781 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 2130 |  | 6853 | -181 |  | 6906 | -181 | -1938 | -1938 | -1938 | Critical Branch | Smoothing ramp | 0 | NA | -53 | 0 | -53 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 2230 |  | 7536 | 625 |  | 7520 | 625 | -2579 | -2579 | -2579 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 16 | 0 | 16 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-07 | May | 2330 |  | 6544 | 404 |  | 6561 | 399 | -1469 | -1469 | -1469 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -17 | 5 | -12 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1230 |  | 5523 | 527 |  | 5523 | 651 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -124 | -124 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1330 |  | 5522 | 250 |  | 5522 | 247 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 3 | 3 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1430 |  | 5523 | 281 |  | 5523 | 335 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -54 | -54 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1530 |  | 5409 | 530 |  | 5409 | 532 | 12081 | -60 | 12081 | ID schedules | ID schedules | 12141 | NA | 0 | -2 | -2 | -60 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1630 |  | 5845 | 652 |  | 5845 | 652 | 11967 | -60 | 11967 | ID schedules | ID schedules | 12027 | NA | 0 | 0 | 0 | -60 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1730 |  | 5845 | 652 |  | 5845 | 652 | 11982 | -60 | 11982 | ID schedules | ID schedules | 12042 | NA | 0 | 0 | 0 | -60 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1830 |  | 5749 | 629 |  | 5749 | 629 | -3420 | -3420 | -3420 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 1930 |  | 5749 | 629 |  | 5749 | 629 | -3425 | -3425 | -3425 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 2030 |  | 5526 | 476 |  | 5526 | 476 | -3224 | -3224 | -3224 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4682 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 2130 |  | 6143 | 748 |  | 6144 | 757 | -3323 | -3323 | -3323 | ID schedules | ID schedules | 0 | NA | -1 | -9 | -10 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5450 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 2230 |  | 6574 | 779 |  | 6574 | 779 | -3566 | -3566 | -3566 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5949 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-08 | May | 2330 |  | 6202 | 672 |  | 6202 | 672 | -3267 | -3267 | -3267 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 5314 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 1230 | 8732 |  |  | 8732 |  |  | -1793 | -1793 | -1793 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -405 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 424 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-09 | May | 1330 | 8732 |  |  | 8732 |  |  | -1793 | -1793 | -1793 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -405 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 424 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-09 | May | 1430 | 8732 |  |  | 8732 |  |  | -1793 | -1793 | -1793 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -405 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 424 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-09 | May | 1530 | 7861 |  |  | 7870 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -9 | NA | NA | NA | 0 | 1 | -416 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 416 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-09 | May | 1630 | 7900 |  |  | 7900 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 1730 | 7862 |  |  | 7902 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -40 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 1830 | 6643 |  |  | 6643 |  |  | 12728 | -63 | 12728 | ID schedules | TTC Validation phase - bilateral reduction | 12791 | 0 | NA | NA | NA | -63 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 1930 | 6643 |  |  | 6643 |  |  | 12728 | -63 | 12728 | ID schedules | TTC Validation phase - bilateral reduction | 12791 | 0 | NA | NA | NA | -63 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 2030 | 6234 |  |  | 6234 |  |  | 13137 | -63 | 12816 | Critical Branch | TTC Validation phase - bilateral reduction | 13200 | 0 | NA | NA | NA | -384 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 2130 | 6947 |  |  | 6947 |  |  | 1371 | 226 | 1174 | Minimum Margin | ID schedules | 1145 | 0 | NA | NA | NA | 29 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 2230 | 6881 |  |  | 6860 |  |  | 1437 | 226 | 1263 | Minimum Margin | ID schedules | 1211 | 21 | NA | NA | NA | 52 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | 6545 | N-1 Albertville-Rondissone 1 / [FR-IT] Albertville-Rondissone 2 [OPP] [FR] | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-09 | May | 2330 | 6343 |  |  | 6343 |  |  | 1945 | 225 | 1753 | Minimum Margin | ID schedules | 1720 | 0 | NA | NA | NA | 33 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 1230 |  | 2675 | 828 |  | 1229 | 828 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1446 | 0 | 1446 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 1330 |  | 2675 | 828 |  | 1374 | 784 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1301 | 44 | 1345 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 1430 |  | 2675 | 828 |  | 1361 | 791 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1314 | 37 | 1351 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 1530 |  | 2064 | 620 |  | 1894 | 567 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 170 | 53 | 223 | 0 | 1 | -361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 402 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-10 | May | 1630 |  | 2088 | 652 |  | 2088 | 652 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | -423 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 423 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-10 | May | 1730 |  | 3038 | 652 |  | 3038 | 652 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-10 | May | 1830 |  | 4429 | 598 |  | 4463 | 598 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -34 | 0 | -34 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 1930 |  | 5932 | 586 |  | 5892 | 586 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 40 | 0 | 40 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 2030 |  | 6393 | 598 |  | 6379 | 598 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 14 | 0 | 14 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 2130 | 6388 |  |  | 6388 |  |  | -4021 | -4021 | -4861 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 2230 | 5822 |  |  | 5822 |  |  | -3455 | -3455 | -4446 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-10 | May | 2330 | 5757 |  |  | 5757 |  |  | -3396 | -3396 | -4103 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-11 | May | 1230 |  | 2767 | 1116 |  | 1398 | 1044 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1369 | 72 | 1441 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 340 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-11 | May | 1330 |  | 2767 | 1116 |  | 1399 | 1044 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1368 | 72 | 1440 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 339 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-11 | May | 1430 |  | 2767 | 1116 |  | 1399 | 1044 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1368 | 72 | 1440 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 340 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-11 | May | 1530 |  | 1957 | 480 |  | 1345 | 462 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 612 | 18 | 630 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 357 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-11 | May | 1630 |  | 1928 | 512 |  | 1928 | 512 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 357 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-11 | May | 1730 |  | 2127 | 673 |  | 2127 | 673 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-11 | May | 1830 |  | 2734 | 849 |  | 2985 | 851 | 9911 | -73 | 9911 | ID schedules | TTC Validation phase - bilateral reduction | 9984 | NA | -251 | -2 | -253 | -73 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-11 | May | 1930 |  | 4234 | 846 |  | 4234 | 846 | 8264 | -73 | 8264 | ID schedules | TTC Validation phase - bilateral reduction | 8337 | NA | 0 | 0 | 0 | -73 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-11 | May | 2030 |  | 5734 | 846 |  | 5734 | 846 | 6577 | -73 | 6577 | ID schedules | TTC Validation phase - bilateral reduction | 6650 | NA | 0 | 0 | 0 | -73 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-11 | May | 2130 | 6437 |  |  | 6437 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-11 | May | 2230 | 6202 |  |  | 6202 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-11 | May | 2330 | 6361 |  |  | 6361 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1230 |  | 7056 | 775 |  | 6622 | 579 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 434 | 196 | 630 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1330 |  | 7056 | 775 |  | 6622 | 535 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 434 | 240 | 674 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1430 |  | 7056 | 775 |  | 6622 | 447 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 434 | 328 | 762 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1530 | 6465 |  |  | 6466 |  |  | 5529 | -49 | 4875 | ID schedules | ID schedules | 5578 | -1 | NA | NA | NA | -703 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1630 | 6732 |  |  | 6736 |  |  | 5262 | -49 | 4825 | ID schedules | ID schedules | 5311 | -4 | NA | NA | NA | -486 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1730 | 6258 |  |  | 6258 |  |  | 5736 | -49 | 4913 | ID schedules | ID schedules | 5785 | 0 | NA | NA | NA | -872 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1830 |  | 5879 | 654 |  | 5879 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 1930 |  | 5865 | 654 |  | 5865 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 2030 |  | 5867 | 654 |  | 5867 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 2130 | 6680 |  |  | 6680 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 2230 | 6682 |  |  | 6682 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-12 | May | 2330 | 6305 |  |  | 6305 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 1230 | 6860 |  |  | 6860 |  |  | 0 | 0 | -2672 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-13 | May | 1330 | 6860 |  |  | 6860 |  |  | 0 | 0 | -2672 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-13 | May | 1430 | 6860 |  |  | 6860 |  |  | 0 | 0 | -2672 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 347 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-13 | May | 1530 | 6248 |  |  | 6248 |  |  | 0 | 0 | 4487 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 4487 | 1 | -313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-13 | May | 1630 | 6248 |  |  | 6248 |  |  | 0 | 0 | 4487 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 4487 | 1 | -313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-13 | May | 1730 | 6248 |  |  | 6248 |  |  | 0 | 0 | 5112 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 5112 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 1830 |  | 6047 | 654 |  | 6047 | 654 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 1930 |  | 6048 | 654 |  | 6048 | 654 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 2030 |  | 5565 | 654 |  | 5565 | 654 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 2130 |  | 6017 | 654 |  | 6017 | 654 | -2903 | -2903 | -2903 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 2230 |  | 6225 | 654 |  | 6225 | 654 | -3221 | -3221 | -3221 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-13 | May | 2330 |  | 5667 | 477 |  | 5667 | 466 | -2497 | -2497 | -2497 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 11 | 11 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-14 | May | 1230 |  | 7047 | -344 |  | 7047 | -142 | -825 | -825 | -825 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -202 | -202 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-14 | May | 1330 |  | 7599 | 114 |  | 7554 | 116 | -1272 | -1272 | -1272 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 45 | -2 | 43 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | 7335 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-14 | May | 1430 |  | 7047 | -340 |  | 7047 | 220 | -800 | -800 | -800 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -560 | -560 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | 6750 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-14 | May | 1530 | 7565 |  |  | 7565 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 1630 | 7565 |  |  | 7565 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 1730 | 7265 |  |  | 7265 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 377 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 1830 | 6343 |  |  | 6343 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 317 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 1930 | 5518 |  |  | 5518 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 308 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 2030 | 5641 |  |  | 5641 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 316 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 2130 | 5548 |  |  | 5630 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | -82 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 267 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 2230 | 5952 |  |  | 5955 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -3 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 333 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-14 | May | 2330 | 5534 |  |  | 5578 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -44 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 300 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-15 | May | 1230 | 7547 |  |  | 7547 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 1330 | 7547 |  |  | 7547 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 1430 | 7547 |  |  | 7547 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 1530 | 7332 |  |  | 7332 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-15 | May | 1630 | 7129 |  |  | 7129 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-15 | May | 1730 | 6704 |  |  | 6704 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-15 | May | 1830 |  | 6001 | 588 |  | 6001 | 597 | 15910 | 0 | 15910 | Critical Branch | TTC Validation phase - bilateral reduction | 15910 | NA | 0 | -9 | -9 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-15 | May | 1930 |  | 6001 | 261 |  | 6001 | 264 | 15821 | 0 | 15821 | Critical Branch | TTC Validation phase - bilateral reduction | 15821 | NA | 0 | -3 | -3 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 2030 |  | 6001 | 654 |  | 6001 | 654 | 15948 | 0 | 15948 | Critical Branch | TTC Validation phase - bilateral reduction | 15948 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 2130 | 7525 |  |  | 7492 |  |  | 0 | 0 | -1423 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 33 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 2230 | 7525 |  |  | 7525 |  |  | 0 | 0 | -1442 | Critical Branch | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-15 | May | 2330 | 6925 |  |  | 6925 |  |  | 0 | 0 | -870 | Critical Branch | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-16 | May | 1230 |  | 6795 | 693 |  | 6026 | 654 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 769 | 39 | 808 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-16 | May | 1330 |  | 6795 | 693 |  | 6006 | 654 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 789 | 39 | 828 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-16 | May | 1430 |  | 6795 | 693 |  | 6006 | 654 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 789 | 39 | 828 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-16 | May | 1530 | 4742 |  |  | 4742 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-16 | May | 1630 | 4742 |  |  | 4742 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-16 | May | 1730 | 4999 |  |  | 4999 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-16 | May | 1830 |  | 5780 | 652 |  | 5999 | 652 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -219 | 0 | -219 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-16 | May | 1930 |  | 6216 | 347 |  | 6216 | 347 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-16 | May | 2030 |  | 6294 | 430 |  | 6294 | 430 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-16 | May | 2130 | 7424 |  |  | 7425 |  |  | -3773 | -3773 | -4348 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-16 | May | 2230 | 7848 |  |  | 7849 |  |  | -4197 | -4197 | -4329 | ID schedules | ID schedules | 0 | -1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-16 | May | 2330 | 7256 |  |  | 7258 |  |  | -3596 | -3596 | -3837 | ID schedules | ID schedules | 0 | -2 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-17 | May | 1230 |  | 1085 | 649 |  | 1351 | 652 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -266 | -3 | -269 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 1330 |  | 2030 | 455 |  | 1666 | 440 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 364 | 15 | 379 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 1430 |  | 2030 | 455 |  | 1648 | 417 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 382 | 38 | 420 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 1530 | 567 |  |  | 567 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-17 | May | 1630 | 532 |  |  | 532 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-17 | May | 1730 | 584 |  |  | 584 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-17 | May | 1830 |  | 2726 | 821 |  | 2702 | 821 | 1515 | 25 | 1515 | Minimum Margin | Smoothing ramp | 1490 | NA | 24 | 0 | 24 | 25 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 1930 |  | 4201 | 818 |  | 4201 | 818 | -46 | -46 | -46 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 2030 |  | 4820 | 775 |  | 4820 | 810 | -960 | -960 | -960 | ID schedules | ID schedules | 0 | NA | 0 | -35 | -35 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 2130 |  | 5878 | 388 |  | 5878 | 388 | -2396 | -2396 | -2396 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 2230 |  | 5845 | 388 |  | 5845 | 388 | -2371 | -2371 | -2371 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-17 | May | 2330 |  | 5659 | 413 |  | 5659 | 413 | -2077 | -2077 | -2077 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 1230 |  | 930 | 677 |  | 643 | 677 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 287 | 0 | 287 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 1330 |  | 511 | 672 |  | 511 | 677 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -5 | -5 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 1430 |  | 1104 | 677 |  | 1103 | 677 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 1530 | 599 |  |  | 599 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-18 | May | 1630 | 598 |  |  | 598 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-18 | May | 1730 | 684 |  |  | 684 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-18 | May | 1830 |  | 2745 | 865 |  | 2745 | 865 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 1930 |  | 4638 | 865 |  | 4245 | 865 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 393 | 0 | 393 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 2030 |  | 5207 | 778 |  | 5464 | 778 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | -257 | 0 | -257 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 2130 |  | 5639 | 865 |  | 5639 | 865 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 2230 |  | 5546 | 763 |  | 5546 | 763 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-18 | May | 2330 |  | 5127 | 775 |  | 5127 | 847 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -72 | -72 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 1230 |  | 4893 | 413 |  | 5195 | 413 | 18928 | 0 | 18928 | Critical Branch | TTC Validation phase - bilateral reduction | 18928 | NA | -302 | 0 | -302 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 307 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 1330 |  | 5261 | 209 |  | 5146 | 209 | 18872 | 0 | 18872 | Critical Branch | TTC Validation phase - bilateral reduction | 18872 | NA | 115 | 0 | 115 | 0 | 1 | 83 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 107 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 1430 |  | 4539 | 99 |  | 4699 | 99 | 18934 | 0 | 18934 | Critical Branch | TTC Validation phase - bilateral reduction | 18934 | NA | -160 | 0 | -160 | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 1530 | 4478 |  |  | 4478 |  |  | 18680 | -29 | 17037 | ID schedules | TTC Validation phase - bilateral reduction | 18709 | 0 | NA | NA | NA | -1672 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 307 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-19 | May | 1630 | 4652 |  |  | 4652 |  |  | 18506 | -29 | 16934 | ID schedules | TTC Validation phase - bilateral reduction | 18535 | 0 | NA | NA | NA | -1601 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 307 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-19 | May | 1730 | 5515 |  |  | 5515 |  |  | 17643 | -29 | 17033 | ID schedules | TTC Validation phase - bilateral reduction | 17672 | 0 | NA | NA | NA | -639 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-19 | May | 1830 |  | 5517 | 772 |  | 5517 | 750 | -4434 | -4434 | -4434 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 22 | 22 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 1930 |  | 5048 | 742 |  | 5048 | 742 | -3580 | -3580 | -3580 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 2030 |  | 4960 | 820 |  | 4960 | 820 | -3428 | -3428 | -3428 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 2130 |  | 4686 | 639 |  | 4724 | 639 | -2974 | -2974 | -2974 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -38 | 0 | -38 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 2230 |  | 5370 | 639 |  | 5370 | 639 | -3694 | -3694 | -3694 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-19 | May | 2330 |  | 4976 | 636 |  | 4976 | 640 | -3639 | -3639 | -3639 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -4 | -4 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-20 | May | 1230 | 6283 |  |  | 6283 |  |  | 0 | 0 | 9579 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 9579 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 315 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1330 | 6283 |  |  | 6283 |  |  | 0 | 0 | 9579 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 9579 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 315 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1430 | 6303 |  |  | 6303 |  |  | 0 | 0 | 9559 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 9559 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 316 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1530 | 6481 |  |  | 6481 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 327 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1630 | 5909 |  |  | 5909 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 327 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1730 | 5887 |  |  | 5887 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 327 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1830 | 6081 |  |  | 6081 |  |  | 0 | 0 | -2799 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 307 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 1930 | 6231 |  |  | 6050 |  |  | 0 | 0 | -2828 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 181 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 122 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 2030 | 6231 |  |  | 5805 |  |  | 0 | 0 | -2679 | Critical Branch | ID schedules | 0 | 426 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-20 | May | 2130 |  | 4542 | 525 |  | 4805 | 525 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -263 | 0 | -263 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-20 | May | 2230 |  | 5542 | 525 |  | 5626 | 525 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -84 | 0 | -84 | 0 | 1 | 114 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 120 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-20 | May | 2330 |  | 5694 | 545 |  | 5714 | 545 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -20 | 0 | -20 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 318 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-21 | May | 1230 | 5137 |  |  | 5259 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -122 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 325 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1330 | 5156 |  |  | 5256 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -100 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 325 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1430 | 5891 |  |  | 5904 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -13 | NA | NA | NA | 0 | 1 | 120 | None | Reduction because NTC over thermal limit on border | 325 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1530 | 5722 |  |  | 5722 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1630 | 6096 |  |  | 6098 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -2 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1730 | 5447 |  |  | 5447 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1830 | 6637 |  |  | 6637 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 1930 | 7296 |  |  | 7296 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 2030 | 7296 |  |  | 7296 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 2130 | 7301 |  |  | 7344 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -43 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 2230 | 7296 |  |  | 7296 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-21 | May | 2330 | 6717 |  |  | 6717 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-22 | May | 1230 | 6093 |  |  | 6093 |  |  | 21243 | -50 | 20783 | ID schedules | ID schedules | 21293 | 0 | NA | NA | NA | -510 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1330 | 6091 |  |  | 6091 |  |  | 21245 | -50 | 20783 | ID schedules | ID schedules | 21295 | 0 | NA | NA | NA | -512 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1430 | 6450 |  |  | 6450 |  |  | 20886 | -50 | 20783 | ID schedules | ID schedules | 20936 | 0 | NA | NA | NA | -153 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1530 | 6244 |  |  | 6244 |  |  | 19924 | -42 | 19918 | ID schedules | ID schedules | 19966 | 0 | NA | NA | NA | -48 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1630 | 6274 |  |  | 6274 |  |  | 20051 | -43 | 20050 | Critical Branch | Critical Branch | 20094 | 0 | NA | NA | NA | -44 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1730 | 6274 |  |  | 6274 |  |  | 20051 | -43 | 20050 | Critical Branch | Critical Branch | 20094 | 0 | NA | NA | NA | -44 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1830 |  | 7227 | -226 |  | 7228 | -226 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -1 | 0 | -1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 1930 |  | 7882 | 304 |  | 7882 | 420 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -116 | -116 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 2030 |  | 7862 | 654 |  | 7862 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 2130 |  | 7765 | 646 |  | 7765 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -8 | -8 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 2230 |  | 7530 | 654 |  | 7519 | 654 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 11 | 0 | 11 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-22 | May | 2330 |  | 7322 | 679 |  | 7322 | 679 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 1230 | 5892 |  |  | 5892 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 325 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-23 | May | 1330 | 5879 |  |  | 5879 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 325 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-23 | May | 1430 | 5885 |  |  | 5885 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 325 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-23 | May | 1530 | 5998 |  |  | 5998 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 307 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-23 | May | 1630 | 5331 |  |  | 5441 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -110 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 307 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 1730 | 6007 |  |  | 6009 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | -2 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 272 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 1830 |  | 6535 | 724 |  | 6535 | 801 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -77 | -77 | 0 | 1 | 123 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 1930 |  | 7628 | 818 |  | 7628 | 818 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 2030 |  | 7177 | 818 |  | 7177 | 818 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 2130 | 7307 |  |  | 7307 |  |  | -2236 | -2236 | -2237 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 2230 | 7307 |  |  | 7307 |  |  | -2236 | -2236 | -2237 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-23 | May | 2330 | 6707 |  |  | 6707 |  |  | -1651 | -1651 | -1652 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-24 | May | 1230 |  | 2202 | 818 |  | 2202 | 818 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-24 | May | 1330 |  | 2196 | 817 |  | 2196 | 817 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-24 | May | 1430 |  | 2202 | 818 |  | 2202 | 818 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-24 | May | 1530 | 1525 |  |  | 1525 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 323 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-24 | May | 1630 | 1528 |  |  | 1528 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-24 | May | 1730 | 1500 |  |  | 1500 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-24 | May | 1830 |  | 3588 | 652 |  | 3588 | 652 | 13278 | -73 | 13278 | ID schedules | TTC Validation phase - bilateral reduction | 13351 | NA | 0 | 0 | 0 | -73 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Reduction due to missing redispatch potential | None | 3729 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-24 | May | 1930 |  | 5705 | 652 |  | 4997 | 652 | 11675 | -73 | 11675 | ID schedules | TTC Validation phase - bilateral reduction | 11748 | NA | 708 | 0 | 708 | -73 | 1 | 58 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 20 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Reduction due to missing redispatch potential | None | 5454 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-24 | May | 2030 |  | 5331 | 2 |  | 5515 | 2 | 11809 | -73 | 11809 | Critical Branch | TTC Validation phase - bilateral reduction | 11882 | NA | -184 | 0 | -184 | -73 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 313 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Reduction due to missing redispatch potential | None | 5264 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-24 | May | 2130 | 6691 |  |  | 6691 |  |  | -941 | -941 | -1540 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 375 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-24 | May | 2230 | 6824 |  |  | 6824 |  |  | -1074 | -1074 | -1786 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 418 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-24 | May | 2330 | 7007 |  |  | 7007 |  |  | -1268 | -1268 | -1627 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 407 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-25 | May | 1230 |  | 1174 | 865 |  | 1452 | 865 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -278 | 0 | -278 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -152 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1330 |  | 1925 | 865 |  | 1925 | 865 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1430 |  | 1240 | 861 |  | 1509 | 862 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -269 | -1 | -270 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1530 |  | 1245 | 865 |  | 1245 | 865 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1630 |  | 1237 | 865 |  | 1234 | 865 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 3 | 0 | 3 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1730 |  | 1213 | 865 |  | 1213 | 865 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1830 |  | 2600 | 775 |  | 2600 | 793 | 768 | -55 | 768 | ID schedules | TTC Validation phase - bilateral reduction | 823 | NA | 0 | -18 | -18 | -55 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-25 | May | 1930 |  | 4488 | 753 |  | 4133 | 753 | -1124 | -1124 | -1124 | ID schedules | Smoothing ramp | 0 | NA | 355 | 0 | 355 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-25 | May | 2030 |  | 5213 | 717 |  | 5213 | 723 | -1900 | -1900 | -1900 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -6 | -6 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-25 | May | 2130 | 7123 |  |  | 6536 |  |  | -1171 | -1171 | -625 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 587 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-25 | May | 2230 | 7123 |  |  | 7123 |  |  | -1171 | -1171 | -1171 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-25 | May | 2330 | 7123 |  |  | 7123 |  |  | -1170 | -1170 | -1169 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 1230 |  | 4158 | 216 |  | 4470 | 216 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -312 | 0 | -312 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-26 | May | 1330 |  | 4825 | 215 |  | 4878 | 215 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -53 | 0 | -53 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-26 | May | 1430 |  | 4293 | 251 |  | 4570 | 251 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -277 | 0 | -277 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-26 | May | 1530 | 4398 |  |  | 4398 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-26 | May | 1630 | 4730 |  |  | 4730 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-26 | May | 1730 | 5666 |  |  | 5666 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 1830 |  | 5543 | 535 |  | 5543 | 533 | -3137 | -3137 | -3137 | ID schedules | ID schedules | 0 | NA | 0 | 2 | 2 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 1930 |  | 5365 | 656 |  | 5365 | 656 | -3062 | -3062 | -3062 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 2030 |  | 4537 | 656 |  | 4863 | 656 | -1834 | -1834 | -1834 | ID schedules | ID schedules | 0 | NA | -326 | 0 | -326 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 2130 |  | 4759 | 460 |  | 4946 | 441 | 1220 | 215 | 1220 | Minimum Margin | ID schedules | 1005 | NA | -187 | 19 | -168 | 215 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2267 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 2230 |  | 5745 | 463 |  | 5626 | 444 | 299 | 215 | 299 | Minimum Margin | TTC Validation phase - bilateral reduction | 84 | NA | 119 | 19 | 138 | 215 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2816 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-26 | May | 2330 |  | 5404 | -214 |  | 5285 | -214 | 720 | 215 | 720 | Minimum Margin | ID schedules | 505 | NA | 119 | 0 | 119 | 215 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 2606 | None | Process fail during TSO validation phase | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 1230 | 7755 |  |  | 7755 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-27 | May | 1330 | 7685 |  |  | 7685 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-27 | May | 1430 | 7755 |  |  | 7755 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-27 | May | 1530 | 6756 |  |  | 6756 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-27 | May | 1630 | 6756 |  |  | 6756 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 1730 | 6862 |  |  | 6862 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 1830 |  | 7164 | -124 |  | 7164 | -124 | -4728 | -4728 | -4728 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 1930 |  | 7164 | 505 |  | 7164 | 466 | -4459 | -4459 | -4459 | ID schedules | ID schedules | 0 | NA | 0 | 39 | 39 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 2030 |  | 6929 | 642 |  | 6929 | 642 | -4113 | -4113 | -4113 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-27 | May | 2130 | 7212 |  |  | 7224 |  |  | -2096 | -2096 | -2086 | ID schedules | ID schedules | 0 | -12 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 2230 | 7132 |  |  | 7132 |  |  | -2016 | -2016 | -1987 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-27 | May | 2330 | 6718 |  |  | 6718 |  |  | -1604 | -1604 | -1575 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1230 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 1 | -298 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 360 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-28 | May | 1330 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1430 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1530 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1630 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1730 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1830 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 1930 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 2030 | 6686 |  |  | 6352 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 334 |  |  | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -80 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-28 | May | 2130 | 6686 |  |  | 6668 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 18 |  |  | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 335 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-28 | May | 2230 | 6686 |  |  | 6686 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-28 | May | 2330 | 6286 |  |  | 6286 |  |  | 0 | 0 | 0 | Scheduled TTC | Scheduled TTC | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1230 | 6143 |  |  | 6143 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1330 | 6143 |  |  | 6143 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1430 | 6143 |  |  | 6143 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1530 | 6237 |  |  | 6237 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1630 | 6453 |  |  | 6462 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -9 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1730 | 6500 |  |  | 6500 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-29 | May | 1830 | 6204 |  |  | 6204 |  |  | 2679 | -33 | 2680 | ID schedules | TTC Validation phase - bilateral reduction | 2712 | 0 |  |  | NA | -32 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 312 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-29 | May | 1930 | 6204 |  |  | 6204 |  |  | 2679 | -33 | 2680 | ID schedules | TTC Validation phase - bilateral reduction | 2712 | 0 |  |  | NA | -32 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 312 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-29 | May | 2030 | 5663 |  |  | 5663 |  |  | 3220 | -33 | 2790 | Critical Branch | TTC Validation phase - bilateral reduction | 3253 | 0 |  |  | NA | -463 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 312 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-29 | May | 2130 | 7059 |  |  | 7007 |  |  | -3353 | -3353 | -3319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 52 |  |  | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 308 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-29 | May | 2230 | 7059 |  |  | 7007 |  |  | -3353 | -3353 | -3319 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 52 |  |  | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 308 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-29 | May | 2330 | 6659 |  |  | 6659 |  |  | -2953 | -2953 | -2953 | Critical Branch | Critical Branch | 0 | 0 |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-30 | May | 1230 |  | 6825 | 748 |  | 5661 | 395 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1164 | 353 | 1517 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1330 |  | 6825 | 748 |  | 5671 | 411 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1154 | 337 | 1491 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1430 |  | 6825 | 748 |  | 5666 | 403 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 1159 | 345 | 1504 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1530 |  | 6525 | 459 |  | 5564 | 360 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 961 | 99 | 1060 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1630 |  | 6525 | 459 |  | 5554 | 348 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 971 | 111 | 1082 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1730 |  | 6525 | 459 |  | 5551 | 357 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 974 | 102 | 1076 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1830 |  | 5405 | 579 |  | 5736 | 579 | -1946 | -1946 | -1946 | ID schedules | ID schedules | 0 | NA | -331 | 0 | -331 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-30 | May | 1930 |  | 6598 | 445 |  | 6598 | 440 | -3250 | -3250 | -3250 | ID schedules | ID schedules | 0 | NA |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-30 | May | 2030 |  | 6802 | 592 |  | 6802 | 592 | -3363 | -3363 | -3363 | ID schedules | ID schedules | 0 | NA |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-30 | May | 2130 |  | 6247 | 654 |  | 6361 | 654 | -3667 | -3667 | -3667 | ID schedules | ID schedules | 0 | NA |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-30 | May | 2230 |  | 6325 | 654 |  | 6328 | 654 | -3781 | -3781 | -3781 | ID schedules | ID schedules | 0 | NA |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-30 | May | 2330 |  | 6354 | 65 |  | 6354 | 61 | -3947 | -3947 | -3947 | ID schedules | ID schedules | 0 | NA |  |  | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-05-31 | May | 1230 |  | 254 | 250 |  | 256 | 250 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -2 | 0 | -2 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-31 | May | 1330 |  | 591 | 253 |  | 591 | 253 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-31 | May | 1430 |  | 252 | 248 |  | 252 | 248 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-31 | May | 1530 | 6153 |  |  | 4791 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 1362 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-31 | May | 1630 | 6153 |  |  | 6153 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-31 | May | 1730 | 6153 |  |  | 5817 |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 0 | 336 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-31 | May | 1830 |  | 3590 | 722 |  | 4064 | 722 | -1518 | -1518 | -1518 | ID schedules | ID schedules | 0 | NA | -474 | 0 | -474 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-31 | May | 1930 |  | 5279 | 722 |  | 5516 | 722 | -3754 | -3754 | -3754 | ID schedules | Smoothing ramp | 0 | NA | -237 | 0 | -237 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-31 | May | 2030 |  | 4828 | 722 |  | 5291 | 722 | -2826 | -2826 | -2826 | ID schedules | ID schedules | 0 | NA | -463 | 0 | -463 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-05-31 | May | 2130 | 4512 |  |  | 4512 |  |  | -2893 | -2893 | -3179 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-31 | May | 2230 | 4512 |  |  | 4512 |  |  | -2893 | -2893 | -3071 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-05-31 | May | 2330 | 4250 |  |  | 4250 |  |  | -2631 | -2631 | -2720 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1230 | 510 |  |  | 510 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1330 | 501 |  |  | 501 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1430 | 500 |  |  | 500 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1530 | 866 |  |  | 866 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1630 | 866 |  |  | 866 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1730 | 1096 |  |  | 1096 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1830 | 6217 |  |  | 3656 |  |  | -2643 | -2643 | -34 | Critical Branch | Smoothing ramp | 0 | 2561 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 1930 | 6217 |  |  | 5235 |  |  | -2643 | -2643 | -1606 | Critical Branch | Smoothing ramp | 0 | 982 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 2030 | 6217 |  |  | 5998 |  |  | -2643 | -2643 | -2402 | Critical Branch | Smoothing ramp | 0 | 219 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 2130 | 5403 |  |  | 5403 |  |  | -1724 | -1724 | -2593 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 2230 | 5403 |  |  | 5403 |  |  | -1724 | -1724 | -2593 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-01 | June | 2330 | 5608 |  |  | 5608 |  |  | -1903 | -1903 | -2683 | Critical Branch | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-02 | June | 1230 |  | 235 | 2864 |  | -67 | 3155 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 302 | -291 | 11 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -96 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 1330 |  | 235 | 2864 |  | 29 | 2864 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 206 | 0 | 206 | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 1430 |  | 235 | 2864 |  | -131 | 3155 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 366 | -291 | 75 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 1530 | 201 |  |  | 201 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 150 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-02 | June | 1630 | 500 |  |  | 1145 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -645 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-02 | June | 1730 | 1500 |  |  | 1500 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-02 | June | 1830 |  | 3504 | 827 |  | 3535 | 827 | 5039 | -16 | 5039 | ID schedules | TTC Validation phase - bilateral reduction | 5055 | NA | -31 | 0 | -31 | -16 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 1930 |  | 5386 | 827 |  | 5098 | 827 | 3263 | -16 | 3263 | ID schedules | TTC Validation phase - bilateral reduction | 3279 | NA | 288 | 0 | 288 | -16 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 2030 |  | 5516 | 827 |  | 5649 | 827 | 3144 | -16 | 3144 | ID schedules | TTC Validation phase - bilateral reduction | 3160 | NA | -133 | 0 | -133 | -16 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 2130 |  | 4664 | 608 |  | 4818 | 608 | -1767 | -1767 | -1767 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -154 | 0 | -154 | 0 | 1 | 108 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -108 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 2230 |  | 5032 | 608 |  | 5032 | 608 | -2730 | -2730 | -2730 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 108 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 221 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-02 | June | 2330 |  | 4663 | 581 |  | 4797 | 603 | -1996 | -1996 | -1996 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | -134 | -22 | -156 | 0 | 1 | 103 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 367 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-03 | June | 1230 | 6241 |  |  | 6121 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 120 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 1330 | 6241 |  |  | 6147 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 94 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 1430 | 6241 |  |  | 6213 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 28 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 371 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 1530 | 6031 |  |  | 6031 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 337 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 1630 | 6546 |  |  | 6546 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 1730 | 6350 |  |  | 6350 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 1830 |  | 5659 | 253 |  | 5659 | 274 | -3834 | -3834 | -3834 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -21 | -21 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-03 | June | 1930 |  | 5659 | 474 |  | 5659 | 474 | -3691 | -3691 | -3691 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | -305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 305 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-03 | June | 2030 |  | 5392 | 474 |  | 5392 | 474 | -3674 | -3674 | -3674 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 38 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-03 | June | 2130 | 5544 |  |  | 5544 |  |  | -2504 | -2504 | -2941 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -323 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 323 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 2230 | 6413 |  |  | 6413 |  |  | -3373 | -3373 | -3370 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-03 | June | 2330 | 5879 |  |  | 5880 |  |  | -2841 | -2841 | -2908 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -1 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1230 | 5956 |  |  | 5956 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1330 | 5956 |  |  | 5956 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1430 | 5956 |  |  | 5956 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1530 | 5956 |  |  | 5956 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1630 | 5956 |  |  | 5956 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1730 | 6477 |  |  | 6477 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 388 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-04 | June | 1830 |  | 5659 | 420 |  | 5659 | 420 | -2384 | -2384 | -2384 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-04 | June | 1930 |  | 5659 | 420 |  | 5659 | 420 | -2319 | -2319 | -2319 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-04 | June | 2030 |  | 5659 | 420 |  | 5659 | 420 | -2319 | -2319 | -2319 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-04 | June | 2130 |  | 5659 | 388 |  | 5659 | 388 | -2705 | -2705 | -2705 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-04 | June | 2230 |  | 5659 | 388 |  | 5659 | 388 | -2771 | -2771 | -2771 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-04 | June | 2330 |  | 5299 | 186 |  | 5299 | 180 | -2528 | -2528 | -2528 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 6 | 6 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1230 | 4883 |  |  | 4883 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1330 | 4883 |  |  | 4883 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1430 | 4884 |  |  | 4884 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1530 | 4775 |  |  | 4775 |  |  | 0 | 0 | 10349 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 10349 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1630 | 4778 |  |  | 4778 |  |  | 0 | 0 | 10349 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 10349 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1730 | 5460 |  |  | 4772 |  |  | 0 | 0 | 9414 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 688 | NA | NA | NA | 9414 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1830 |  | 5922 | 526 |  | 5922 | 462 | -2351 | -2351 | -2351 | ID schedules | ID schedules | 0 | NA | 0 | 64 | 64 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 1930 |  | 6151 | 527 |  | 6151 | 527 | -2588 | -2588 | -2588 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 2030 |  | 6151 | 527 |  | 6151 | 527 | -2588 | -2588 | -2588 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 2130 |  | 6501 | 653 |  | 6501 | 631 | -3099 | -3099 | -3099 | ID schedules | ID schedules | 0 | NA | 0 | 22 | 22 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 2230 |  | 6501 | 184 |  | 6501 | 191 | -3372 | -3372 | -3372 | ID schedules | ID schedules | 0 | NA | 0 | -7 | -7 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-05 | June | 2330 |  | 6138 | 21 |  | 6138 | 21 | -3113 | -3113 | -3113 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1230 | 6881 |  |  | 5354 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1527 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1330 | 6881 |  |  | 5354 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 1527 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1430 | 6881 |  |  | 6881 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1530 |  | 5329 | 243 |  | 5132 | 243 | 1028 | 197 | 1028 | Minimum Margin | TTC Validation phase - bilateral reduction | 831 | NA | 197 | 0 | 197 | 197 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1630 |  | 5338 | 554 |  | 5133 | 537 | 1468 | 197 | 1468 | Minimum Margin | TTC Validation phase - bilateral reduction | 1271 | NA | 205 | 17 | 222 | 197 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1730 |  | 5330 | 145 |  | 5133 | 128 | 1285 | 197 | 1285 | Minimum Margin | TTC Validation phase - bilateral reduction | 1088 | NA | 197 | 17 | 214 | 197 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | 1700 | None | Planned outage of Chaffard-Grande-Ile 2 | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1830 |  | 7150 | 233 |  | 6575 | 233 | -4906 | -4906 | -4906 | Critical Branch | Smoothing ramp | 0 | NA | 575 | 0 | 575 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 1930 |  | 7150 | 527 |  | 7150 | 527 | -4906 | -4906 | -4906 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 2030 |  | 7150 | 522 |  | 7150 | 522 | -4906 | -4906 | -4906 | Critical Branch | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 2130 |  | 7497 | 672 |  | 7499 | 672 | -6116 | -6116 | -6116 | ID schedules | ID schedules | 0 | NA | -2 | 0 | -2 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 2230 |  | 7831 | 672 |  | 7831 | 672 | -6274 | -6274 | -6274 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-06 | June | 2330 |  | 7470 | 260 |  | 7470 | 260 | -5896 | -5896 | -5896 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 7127 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-07 | June | 1230 | 2316 |  |  | 2006 |  |  | 11437 | -55 | 11528 | Critical Branch | Smoothing ramp | 11492 | 310 | NA | NA | NA | 36 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-07 | June | 1330 | 2316 |  |  | 1982 |  |  | 11437 | -55 | 11579 | Critical Branch | TTC Validation phase - bilateral reduction | 11492 | 334 | NA | NA | NA | 87 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-07 | June | 1430 | 2316 |  |  | 2000 |  |  | 11437 | -55 | 11441 | Critical Branch | TTC Validation phase - bilateral reduction | 11492 | 316 | NA | NA | NA | -51 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-07 | June | 1530 | 2060 |  |  | 2060 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 0 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-07 | June | 1630 | 3402 |  |  | 3402 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-07 | June | 1730 | 4780 |  |  | 4780 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-07 | June | 1830 |  | 7397 | 654 |  | 7086 | 654 | -1022 | -1022 | -1022 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 311 | 0 | 311 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-07 | June | 1930 |  | 7739 | 654 |  | 7739 | 654 | -1280 | -1280 | -1280 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-07 | June | 2030 |  | 7854 | 654 |  | 7854 | 654 | -1380 | -1380 | -1380 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-07 | June | 2130 |  | 7927 | 654 |  | 7913 | 654 | -1303 | -1303 | -1303 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 14 | 0 | 14 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-07 | June | 2230 |  | 7927 | 617 |  | 7913 | 621 | -1303 | -1303 | -1303 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 14 | -4 | 10 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-07 | June | 2330 |  | 7587 | 75 |  | 7534 | 75 | -950 | -950 | -950 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 53 | 0 | 53 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 1230 |  | 1243 | 867 |  | 1243 | 867 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-08 | June | 1330 |  | 1243 | 867 |  | 1243 | 867 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-08 | June | 1430 |  | 1243 | 867 |  | 1243 | 867 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-08 | June | 1530 |  | 1614 | 684 |  | 1614 | 720 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | -36 | -36 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 33 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-08 | June | 1630 |  | 2515 | 684 |  | 2515 | 720 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -36 | -36 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-08 | June | 1730 |  | 3015 | 684 |  | 3015 | 720 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -36 | -36 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 1830 | 4000 |  |  | 4000 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 1930 | 5500 |  |  | 5500 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 2030 | 6226 |  |  | 6226 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 2130 |  | 8046 | 669 |  | 7910 | 669 | -1781 | -1781 | -1781 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 136 | 0 | 136 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 2230 |  | 8189 | 517 |  | 8153 | 517 | -1803 | -1803 | -1803 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 36 | 0 | 36 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-08 | June | 2330 |  | 8154 | -172 |  | 8154 | -172 | -1845 | -1845 | -1845 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-09 | June | 1230 | 6362 |  |  | 6362 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-09 | June | 1330 | 6289 |  |  | 6173 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 0 | 116 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-09 | June | 1430 | 6366 |  |  | 6366 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -333 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 333 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-09 | June | 1530 | 7802 |  |  | 7802 |  |  | -2617 | -2617 | -2772 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-09 | June | 1630 | 7802 |  |  | 7802 |  |  | -2617 | -2617 | -2772 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-09 | June | 1730 | 7231 |  |  | 6421 |  |  | -2046 | -2046 | -1899 | Critical Branch | Smoothing ramp | 0 | 810 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-09 | June | 1830 |  | 5659 | 326 |  | 5659 | 350 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -24 | -24 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-09 | June | 1930 |  | 5659 | 106 |  | 5659 | 99 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 7 | 7 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-09 | June | 2030 |  | 5659 | 398 |  | 5659 | 398 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-09 | June | 2130 |  | 5547 | 264 |  | 5547 | 264 | 0 | 0 | 0 | ID schedules | Smoothing ramp | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-09 | June | 2230 |  | 5659 | 101 |  | 5659 | 91 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 10 | 10 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-09 | June | 2330 |  | 5299 | -180 |  | 5299 | -178 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -2 | -2 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1230 | 7009 |  |  | 6885 |  |  | 0 | 0 | -3700 | Critical Branch | Validation phase | 0 | 124 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 6635 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1330 | 7009 |  |  | 7009 |  |  | 0 | 0 | -3824 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1430 | 7009 |  |  | 7009 |  |  | 0 | 0 | -3824 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1530 | 7046 |  |  | 7033 |  |  | 0 | 0 | 13116 | Critical Branch | ID schedules | 0 | 13 | NA | NA | NA | 13116 | 1 | None | None | None | None | None | None | None | 6710 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1630 | 7046 |  |  | 6982 |  |  | 0 | 0 | 13067 | Critical Branch | ID schedules | 0 | 64 | NA | NA | NA | 13067 | 1 | None | None | None | None | None | None | None | 6710 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1730 | 7046 |  |  | 6751 |  |  | 0 | 0 | 13401 | Critical Branch | Smoothing ramp | 0 | 295 | NA | NA | NA | 13401 | 1 | None | None | None | None | None | None | None | 6710 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1830 |  | 4775 | 272 |  | 4775 | 271 | 3878 | 0 | 3878 | ID schedules | ID schedules | 3878 | NA | 0 | 1 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 1930 |  | 4775 | 392 |  | 4775 | 392 | 3878 | 0 | 3878 | ID schedules | ID schedules | 3878 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 2030 |  | 4775 | 392 |  | 4775 | 392 | 3878 | 0 | 3878 | ID schedules | ID schedules | 3878 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 2130 | 6904 |  |  | 6751 |  |  | -4853 | -4853 | -4700 | Critical Branch | Smoothing ramp | 0 | 153 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 2230 | 6904 |  |  | 6904 |  |  | -4853 | -4853 | -4853 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-10 | June | 2330 | 6504 |  |  | 6504 |  |  | -4453 | -4453 | -4453 | Critical Branch | Critical Branch | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1230 | 7205 |  |  | 7139 |  |  | -1751 | -1751 | -1675 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 66 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1330 | 7205 |  |  | 7139 |  |  | -1751 | -1751 | -1675 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 66 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1430 | 7205 |  |  | 7139 |  |  | -1751 | -1751 | -1675 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 66 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1530 | 6373 |  |  | 6373 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1630 | 6373 |  |  | 6373 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1730 | 7273 |  |  | 7273 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-11 | June | 1830 |  | 7961 | 221 |  | 7961 | 221 | -2593 | -2593 | -2593 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-11 | June | 1930 |  | 7961 | 813 |  | 7961 | 813 | -2317 | -2317 | -2317 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 134 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-11 | June | 2030 |  | 7404 | 834 |  | 7404 | 834 | -1936 | -1936 | -1936 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 132 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -132 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-11 | June | 2130 |  | 7234 | 783 |  | 7138 | 783 | -1480 | -1480 | -1480 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 96 | 0 | 96 | 0 | 1 | 135 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -135 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-11 | June | 2230 |  | 7604 | 774 |  | 7604 | 774 | -1686 | -1686 | -1686 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 135 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-11 | June | 2330 |  | 7325 | 254 |  | 7325 | 254 | -1520 | -1520 | -1520 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-12 | June | 1230 | 7200 |  |  | 7200 |  |  | -3019 | -3019 | -3019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-12 | June | 1330 | 7200 |  |  | 7200 |  |  | -3019 | -3019 | -3019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-12 | June | 1430 | 7200 |  |  | 7200 |  |  | -3019 | -3019 | -3019 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-12 | June | 1530 | 6760 |  |  | 6760 |  |  | 12119 | -26 | 12119 | ID schedules | TTC Validation phase - bilateral reduction | 12145 | 0 | NA | NA | NA | -26 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5732 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia [DIR][IT], C: N-2 Divaca-Redipuglia + Divaca-Padriciano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-12 | June | 1630 | 6760 |  |  | 6760 |  |  | 12119 | -26 | 12119 | ID schedules | TTC Validation phase - bilateral reduction | 12145 | 0 | NA | NA | NA | -26 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6509 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-12 | June | 1730 | 6760 |  |  | 6760 |  |  | 12119 | -26 | 12119 | ID schedules | TTC Validation phase - bilateral reduction | 12145 | 0 | NA | NA | NA | -26 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 397 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6509 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-12 | June | 1830 |  | 6866 | 718 |  | 6836 | 718 | -1593 | -1593 | -1593 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 30 | 0 | 30 | 0 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 401 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-12 | June | 1930 |  | 6866 | 718 |  | 6830 | 718 | -1593 | -1593 | -1593 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 36 | 0 | 36 | 0 | 1 | 137 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 395 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-12 | June | 2030 |  | 6866 | 718 |  | 6295 | 718 | -1593 | -1593 | -1593 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 571 | 0 | 571 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-12 | June | 2130 |  | 7540 | 654 |  | 7236 | 654 | -2829 | -2829 | -2829 | ID schedules | ID schedules | 0 | NA | 304 | 0 | 304 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -20 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-12 | June | 2230 |  | 7682 | 654 |  | 7682 | 654 | -3088 | -3088 | -3088 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-12 | June | 2330 |  | 7322 | 611 |  | 7322 | 606 | -2702 | -2702 | -2702 | ID schedules | ID schedules | 0 | NA | 0 | 5 | 5 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | None | 7008 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-13 | June | 1230 | 8328 |  |  | 6629 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1699 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 342 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6616 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-13 | June | 1330 | 8328 |  |  | 6629 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1699 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 342 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6131 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-13 | June | 1430 | 8328 |  |  | 6629 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1699 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 342 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 5735 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 NAUDERS-WESTTIROL 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-13 | June | 1530 | 8328 |  |  | 8030 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 298 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7209 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-13 | June | 1630 | 8328 |  |  | 8030 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 298 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-13 | June | 1730 | 8328 |  |  | 8315 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 13 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-13 | June | 1830 |  | 8189 | -52 |  | 8189 | -52 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-13 | June | 1930 |  | 8189 | 643 |  | 8189 | 643 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-13 | June | 2030 |  | 7969 | 643 |  | 7968 | 643 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 1 | 0 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-13 | June | 2130 | 8328 |  |  | 8328 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-13 | June | 2230 | 8328 |  |  | 8328 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-13 | June | 2330 | 7991 |  |  | 7994 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | -3 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-14 | June | 1230 |  | 3809 | 173 |  | 3330 | 173 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 479 | 0 | 479 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 345 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-14 | June | 1330 |  | 3809 | 173 |  | 3566 | 173 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 243 | 0 | 243 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 345 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-14 | June | 1430 |  | 3927 | 374 |  | 3813 | 374 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 114 | 0 | 114 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 345 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-14 | June | 1530 |  | 6391 | 620 |  | 3991 | 620 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 2400 | 0 | 2400 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 417 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-14 | June | 1630 |  | 5918 | 651 |  | 5364 | 651 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 554 | 0 | 554 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-14 | June | 1730 |  | 6574 | 637 |  | 6574 | 637 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-14 | June | 1830 |  | 8166 | 667 |  | 8166 | 667 | -1092 | -1092 | -1092 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-14 | June | 1930 |  | 8613 | 667 |  | 8613 | 667 | -1324 | -1324 | -1324 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-14 | June | 2030 |  | 8253 | 667 |  | 8253 | 667 | -1276 | -1276 | -1276 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-14 | June | 2130 |  | 8491 | 651 |  | 8491 | 651 | -1419 | -1419 | -1419 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-14 | June | 2230 |  | 8490 | 651 |  | 8490 | 651 | -1418 | -1418 | -1418 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-14 | June | 2330 |  | 7931 | 490 |  | 7931 | 490 | -1186 | -1186 | -1186 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-15 | June | 1230 |  | 4203 | 1979 |  | 1566 | 1979 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 2637 | 0 | 2637 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 394 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-15 | June | 1330 |  | 4203 | 1979 |  | 1566 | 1979 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 2637 | 0 | 2637 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 394 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-15 | June | 1430 |  | 4203 | 1979 |  | 1062 | 1979 | 0 | 0 | 0 | GSK Limitation | ID schedules | 0 | NA | 3141 | 0 | 3141 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 193 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-15 | June | 1530 |  | 2545 | 179 |  | 2545 | 183 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -4 | -4 | 0 | 1 | 24 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 9 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-15 | June | 1630 |  | 4539 | 862 |  | 4539 | 862 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-15 | June | 1730 |  | 5757 | 862 |  | 5757 | 862 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-15 | June | 1830 | 9022 |  |  | 7000 |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 0 | 2022 | NA | NA | NA | 0 | 1 | 157 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8054 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-15 | June | 1930 | 9022 |  |  | 7892 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 1130 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8609 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-15 | June | 2030 | 9022 |  |  | 8783 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 239 | NA | NA | NA | 0 | 1 | 158 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | 8550 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-15 | June | 2130 | 9022 |  |  | 8937 |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 0 | 85 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | 8714 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-15 | June | 2230 | 9022 |  |  | 8992 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-15 | June | 2330 | 9022 |  |  | 8992 |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 0 | 30 | NA | NA | NA | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 1230 | 7377 |  |  | 7377 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-16 | June | 1330 | 7377 |  |  | 7377 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-16 | June | 1430 | 7377 |  |  | 7377 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-16 | June | 1530 | 6933 |  |  | 6933 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -325 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 325 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-16 | June | 1630 | 6933 |  |  | 6933 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 1730 | 6933 |  |  | 6933 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 1830 |  | 7271 | 556 |  | 7271 | 556 | 6600 | 0 | 6600 | ID schedules | TTC Validation phase - bilateral reduction | 6600 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 1930 |  | 7271 | 585 |  | 7271 | 585 | 6600 | 0 | 6600 | ID schedules | TTC Validation phase - bilateral reduction | 6600 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 2030 |  | 7071 | 585 |  | 7070 | 585 | 6599 | 0 | 6599 | ID schedules | TTC Validation phase - bilateral reduction | 6599 | NA | 1 | 0 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 2130 |  | 7829 | 605 |  | 7829 | 605 | 270 | 0 | 270 | Critical Branch | TTC Validation phase - bilateral reduction | 270 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 2230 |  | 7829 | 605 |  | 7829 | 605 | 270 | 0 | 270 | Critical Branch | TTC Validation phase - bilateral reduction | 270 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-16 | June | 2330 |  | 7269 | 630 |  | 7269 | 630 | 856 | 0 | 856 | Critical Branch | TTC Validation phase - bilateral reduction | 856 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 1230 | 8228 |  |  | 8228 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 361 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6488 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-17 | June | 1330 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6171 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-17 | June | 1430 | 8900 |  |  | 8900 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 6486 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-17 | June | 1530 | 9264 |  |  | 8900 |  |  | 1513 | 364 | 1513 | Minimum Margin | TTC Validation phase - bilateral reduction | 1149 | 364 | NA | NA | NA | 364 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8323 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-17 | June | 1630 | 9264 |  |  | 8900 |  |  | 1513 | 364 | 1513 | Minimum Margin | TTC Validation phase - bilateral reduction | 1149 | 364 | NA | NA | NA | 364 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 8748 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-17 | June | 1730 | 9264 |  |  | 9246 |  |  | 1513 | 364 | 1163 | Minimum Margin | TTC Validation phase - bilateral reduction | 1149 | 18 | NA | NA | NA | 14 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 1830 |  | 8035 | 784 |  | 8035 | 808 | -46 | -46 | -46 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -24 | -24 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 1930 |  | 8325 | 845 |  | 8035 | 816 | 290 | 290 | 290 | Adjustment reached | TTC Validation phase - bilateral reduction | 0 | NA | 290 | 29 | 319 | 290 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 173 | None | Reduction because NTC over thermal limit on border | None | None | Reduction due to missing redispatch potential | None | 7555 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 2030 |  | 8252 | 850 |  | 7906 | 844 | 584 | 343 | 584 | Minimum Margin | TTC Validation phase - bilateral reduction | 241 | NA | 346 | 6 | 352 | 343 | 1 | 140 | None | Reduction because NTC over thermal limit on border | -47 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 2130 |  | 8017 | 816 |  | 8017 | 816 | -1549 | -1549 | -1549 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 2230 |  | 7655 | 816 |  | 7609 | 816 | -1357 | -1357 | -1357 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 46 | 0 | 46 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 7390 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-17 | June | 2330 |  | 7417 | 862 |  | 7417 | 862 | -996 | -996 | -996 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1230 | 7424 |  |  | 7424 |  |  | 0 | 0 | -1945 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1330 | 7424 |  |  | 7424 |  |  | 0 | 0 | -1945 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1430 | 7424 |  |  | 7424 |  |  | 0 | 0 | -1945 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1530 | 8781 |  |  | 8781 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 419 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7846 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-18 | June | 1630 | 8781 |  |  | 8781 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1730 | 8500 |  |  | 8500 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1830 |  | 6565 | 502 |  | 6565 | 502 | 6258 | -63 | 6258 | ID schedules | TTC Validation phase - bilateral reduction | 6321 | NA | 0 | 0 | 0 | -63 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 6314 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 1930 |  | 6457 | 494 |  | 6457 | 494 | 6459 | -63 | 6459 | ID schedules | TTC Validation phase - bilateral reduction | 6522 | NA | 0 | 0 | 0 | -63 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 6206 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 2030 |  | 6478 | 495 |  | 6478 | 495 | 6441 | -63 | 6441 | ID schedules | TTC Validation phase - bilateral reduction | 6504 | NA | 0 | 0 | 0 | -63 | 1 | None | None | None | None | None | None | None | None | Reduction due to missing redispatch potential | None | 6227 | Reduction due to missing redispatch potential | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 2130 |  | 7247 | 599 |  | 7096 | 599 | 1058 | 246 | 1058 | Minimum Margin | TTC Validation phase - bilateral reduction | 812 | NA | 151 | 0 | 151 | 246 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 2230 |  | 7760 | 599 |  | 7515 | 599 | 789 | 246 | 789 | Minimum Margin | TTC Validation phase - bilateral reduction | 543 | NA | 245 | 0 | 245 | 246 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-18 | June | 2330 |  | 7200 | 548 |  | 7198 | 548 | 1132 | 246 | 1132 | Minimum Margin | TTC Validation phase - bilateral reduction | 886 | NA | 2 | 0 | 2 | 246 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-19 | June | 1230 | 7260 |  |  | 7239 |  |  | -698 | -698 | -676 | Critical Branch | ID schedules | 0 | 21 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-19 | June | 1330 | 7260 |  |  | 7239 |  |  | -698 | -698 | -676 | Critical Branch | ID schedules | 0 | 21 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-19 | June | 1430 | 7260 |  |  | 7239 |  |  | -698 | -698 | -676 | Critical Branch | ID schedules | 0 | 21 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-19 | June | 1530 | 8265 |  |  | 7911 |  |  | -1213 | -1213 | -866 | Critical Branch | ID schedules | 0 | 354 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 7724 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-19 | June | 1630 | 8265 |  |  | 8187 |  |  | -1213 | -1213 | -1144 | Critical Branch | ID schedules | 0 | 78 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-19 | June | 1730 | 8265 |  |  | 8187 |  |  | -1213 | -1213 | -1144 | Critical Branch | ID schedules | 0 | 78 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-19 | June | 1830 |  | 8727 | 755 |  | 8635 | 755 | -6049 | -6049 | -6049 | Critical Branch | ID schedules | 0 | NA | 92 | 0 | 92 | 0 | 1 | 135 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-19 | June | 1930 |  | 8847 | 755 |  | 8836 | 755 | -6113 | -6113 | -6113 | Critical Branch | ID schedules | 0 | NA | 11 | 0 | 11 | 0 | 1 | 135 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-19 | June | 2030 |  | 8801 | 755 |  | 8306 | 755 | -6110 | -6110 | -6110 | Critical Branch | ID schedules | 0 | NA | 495 | 0 | 495 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-19 | June | 2130 |  | 8575 | 693 |  | 8555 | 693 | -337 | -337 | -337 | Critical Branch | ID schedules | 0 | NA | 20 | 0 | 20 | 0 | 1 | 138 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-19 | June | 2230 |  | 8575 | 693 |  | 8555 | 693 | -337 | -337 | -337 | Critical Branch | ID schedules | 0 | NA | 20 | 0 | 20 | 0 | 1 | 138 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-19 | June | 2330 |  | 8249 | 735 |  | 8178 | 735 | 214 | 214 | 214 | Adjustment reached | ID schedules | 0 | NA | 71 | 0 | 71 | 214 | 1 | 158 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-20 | June | 1230 | 7877 |  |  | 7877 |  |  | -4827 | -4827 | -4827 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-20 | June | 1330 | 7877 |  |  | 7877 |  |  | -4827 | -4827 | -4827 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-20 | June | 1430 | 7877 |  |  | 7877 |  |  | -4827 | -4827 | -4827 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | -373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 373 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-20 | June | 1530 | 8998 |  |  | 8932 |  |  | -6409 | -6409 | -6315 | Critical Branch | ID schedules | 0 | 66 | NA | NA | NA | 0 | 1 | -364 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 364 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-20 | June | 1630 | 8998 |  |  | 8993 |  |  | -6409 | -6409 | -6400 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 5 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 1730 | 8998 |  |  | 8993 |  |  | -6409 | -6409 | -6400 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 5 | NA | NA | NA | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 1830 |  | 7590 | 617 |  | 7590 | 629 | 2810 | -81 | 2810 | ID schedules | TTC Validation phase - bilateral reduction | 2891 | NA | 0 | -12 | -12 | -81 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 1930 |  | 7590 | 816 |  | 7590 | 816 | 2797 | -81 | 2797 | ID schedules | TTC Validation phase - bilateral reduction | 2878 | NA | 0 | 0 | 0 | -81 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 2030 |  | 7525 | 816 |  | 7555 | 816 | 2936 | -81 | 2936 | ID schedules | TTC Validation phase - bilateral reduction | 3017 | NA | -30 | 0 | -30 | -81 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 2130 | 8718 |  |  | 8718 |  |  | -6268 | -6268 | -6267 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 2230 | 8718 |  |  | 8718 |  |  | -6268 | -6268 | -6267 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-20 | June | 2330 | 8118 |  |  | 8117 |  |  | -5664 | -5664 | -5663 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-21 | June | 1230 | 4958 |  |  | 4500 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 458 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 326 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 3288 | Missing CNEC in CC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 NAUDERS-WESTTIROL 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-21 | June | 1330 | 4958 |  |  | 4537 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 421 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 326 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-21 | June | 1430 | 4958 |  |  | 4535 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | 423 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 326 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-21 | June | 1530 |  | 7113 | 654 |  | 5042 | 654 | -825 | -825 | -825 | Critical Branch | ID schedules | 0 | NA | 2071 | 0 | 2071 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 318 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-21 | June | 1630 |  | 7181 | 654 |  | 6922 | 654 | -792 | -792 | -792 | Critical Branch | ID schedules | 0 | NA | 259 | 0 | 259 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 380 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-21 | June | 1730 |  | 6997 | 654 |  | 6740 | 654 | -639 | -639 | -639 | Critical Branch | ID schedules | 0 | NA | 257 | 0 | 257 | 0 | 1 | 139 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 380 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-21 | June | 1830 |  | 7481 | 575 |  | 7482 | 575 | -299 | -299 | -299 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -1 | 0 | -1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-21 | June | 1930 |  | 8190 | 650 |  | 8190 | 650 | -624 | -624 | -624 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 7789 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-21 | June | 2030 |  | 7472 | 667 |  | 7397 | 667 | 397 | 214 | 397 | Minimum Margin | TTC Validation phase - bilateral reduction | 183 | NA | 75 | 0 | 75 | 214 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-21 | June | 2130 |  | 7330 | 773 |  | 7330 | 781 | 1547 | 206 | 1547 | Minimum Margin | TTC Validation phase - bilateral reduction | 1341 | NA | 0 | -8 | -8 | 206 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-21 | June | 2230 |  | 7330 | 773 |  | 7330 | 781 | 1547 | 206 | 1547 | Minimum Margin | TTC Validation phase - bilateral reduction | 1341 | NA | 0 | -8 | -8 | 206 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-21 | June | 2330 |  | 6538 | 804 |  | 6332 | 668 | 2159 | 206 | 2159 | Minimum Margin | ID schedules | 1953 | NA | 206 | 136 | 342 | 206 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | 4986 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 1230 |  | 2607 | 292 |  | 2330 | 380 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 277 | -88 | 189 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 1330 |  | 2306 | 364 |  | 2349 | 416 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -43 | -52 | -95 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 1430 |  | 2607 | 292 |  | 2000 | 292 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 607 | 0 | 607 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 1530 |  | 4786 | 882 |  | 3126 | 879 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1660 | 3 | 1663 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 409 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 1630 |  | 4392 | 974 |  | 4393 | 957 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | -1 | 17 | 16 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | -91 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 1730 |  | 5816 | 974 |  | 5816 | 952 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 22 | 22 | 0 | 1 | 155 | None | Because of high redispatch the leftover intraday capacity was set to 0 | -142 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-22 | June | 1830 |  | 7209 | 781 |  | 7180 | 781 | -218 | -218 | -218 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 29 | 0 | 29 | 0 | 1 | -415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-22 | June | 1930 |  | 7907 | 781 |  | 7907 | 781 | -730 | -730 | -730 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 2030 |  | 8118 | 751 |  | 8108 | 763 | -817 | -817 | -817 | ID schedules | ID schedules | 0 | NA | 10 | -12 | -2 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 7740 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 2130 |  | 8045 | 730 |  | 8058 | 746 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | -13 | -16 | -29 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 7699 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 2230 |  | 8118 | 277 |  | 8118 | 289 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -12 | -12 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-22 | June | 2330 |  | 8118 | -234 |  | 8118 | -230 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -4 | -4 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 1230 | 5153 |  |  | 5153 |  |  | 0 | 0 | -3670 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 1330 | 5153 |  |  | 5153 |  |  | 0 | 0 | -3670 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 4629 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 1430 | 5153 |  |  | 5153 |  |  | 0 | 0 | -3670 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 4639 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 1530 | 6654 |  |  | 6654 |  |  | 0 | 0 | -4107 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | 5995 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 1630 | 6808 |  |  | 6808 |  |  | -4261 | -4261 | -4261 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -201 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 201 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-23 | June | 1730 | 7699 |  |  | 7715 |  |  | -5221 | -5221 | -5235 | ID schedules | ID schedules | 0 | -16 | NA | NA | NA | 0 | 1 | -410 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 410 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2025-06-23 | June | 1830 |  | 8356 | 713 |  | 8356 | 713 | -2667 | -2667 | -2667 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | 6563 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2025-06-23 | June | 1930 |  | 8356 | 673 |  | 8356 | 680 | -2595 | -2595 | -2595 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | -7 | -7 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | 7506 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 2030 |  | 8356 | 669 |  | 8356 | 669 | -2484 | -2484 | -2484 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 2130 | 8666 |  |  | 8654 |  |  | 1050 | 216 | 841 | Minimum Margin | TTC Validation phase - bilateral reduction | 834 | 12 | NA | NA | NA | 7 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 2230 | 8666 |  |  | 8654 |  |  | 1050 | 216 | 841 | Minimum Margin | TTC Validation phase - bilateral reduction | 834 | 12 | NA | NA | NA | 7 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2025-06-23 | June | 2330 | 8065 |  |  | 8053 |  |  | 1639 | 215 | 1431 | Minimum Margin | TTC Validation phase - bilateral reduction | 1424 | 12 | NA | NA | NA | 7 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1230 | 6847 |  |  | 6846 |  |  | 0 | 0 | -3286 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1330 | 6847 |  |  | 6846 |  |  | 0 | 0 | -3286 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1430 | 6847 |  |  | 6846 |  |  | 0 | 0 | -3286 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1530 | 6287 |  |  | 6286 |  |  | 0 | 0 | -4210 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1630 | 7287 |  |  | 7286 |  |  | 0 | 0 | -5218 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1730 | 7287 |  |  | 7286 |  |  | 0 | 0 | -5218 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 1 | -274 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 369 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-24 | June | 1830 |  | 7209 | 664 |  | 7209 | 664 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 1930 |  | 8230 | 698 |  | 8230 | 698 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | 7433 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 2030 |  | 8231 | 698 |  | 8231 | 698 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | 7570 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 2130 |  | 7558 | 719 |  | 7558 | 719 | -1275 | -1275 | -1275 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 2230 |  | 7558 | 719 |  | 7558 | 719 | -1275 | -1275 | -1275 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-24 | June | 2330 |  | 7017 | 744 |  | 6978 | 744 | -672 | -672 | -672 | Critical Branch | Min import NTC Threshold | 0 | NA | 39 | 0 | 39 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 1230 | 7629 |  |  | 7613 |  |  | -4286 | -4286 | -4254 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 372 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-25 | June | 1330 | 7629 |  |  | 7613 |  |  | -4286 | -4286 | -4254 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 372 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-25 | June | 1430 | 7629 |  |  | 7613 |  |  | -4286 | -4286 | -4254 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 16 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 372 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-25 | June | 1530 | 8238 |  |  | 8181 |  |  | -2128 | -2128 | -2096 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 57 | NA | NA | NA | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 365 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-25 | June | 1630 | 8238 |  |  | 8237 |  |  | -2128 | -2128 | -2127 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 1730 | 8838 |  |  | 8837 |  |  | -2719 | -2719 | -2718 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 1830 |  | 8688 | 718 |  | 8271 | 718 | 0 | 0 | 0 | GSK Limitation | Full import calculation | 0 | NA | 417 | 0 | 417 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 1930 |  | 8688 | 718 |  | 8271 | 718 | 0 | 0 | 0 | GSK Limitation | Full import calculation | 0 | NA | 417 | 0 | 417 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 2030 |  | 8688 | 718 |  | 8271 | 718 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 417 | 0 | 417 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 2130 |  | 7767 | 951 |  | 7767 | 926 | -1553 | -1553 | -1553 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 25 | 25 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 192 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 2230 |  | 7767 | 951 |  | 7767 | 926 | -1553 | -1553 | -1553 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 25 | 25 | 0 | 1 | 140 | None | Reduction because NTC over thermal limit on border | 192 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-25 | June | 2330 |  | 7050 | 996 |  | 6944 | 969 | -958 | -958 | -958 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 106 | 27 | 133 | 0 | 1 | 160 | None | Reduction because NTC over thermal limit on border | 369 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-26 | June | 1230 | 7194 |  |  | 7194 |  |  | 246 | -89 | 246 | ID schedules | TTC Validation phase - bilateral reduction | 335 | 0 | NA | NA | NA | -89 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-26 | June | 1330 | 7194 |  |  | 7194 |  |  | 246 | -89 | 246 | ID schedules | TTC Validation phase - bilateral reduction | 335 | 0 | NA | NA | NA | -89 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-26 | June | 1430 | 7194 |  |  | 7194 |  |  | 246 | -89 | 246 | ID schedules | TTC Validation phase - bilateral reduction | 335 | 0 | NA | NA | NA | -89 | 1 | -406 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 406 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-26 | June | 1530 |  | 7033 | 668 |  | 7033 | 668 | -2134 | -2134 | -2134 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 1630 |  | 7071 | 668 |  | 7043 | 668 | -2141 | -2141 | -2141 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 28 | 0 | 28 | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 1730 |  | 8471 | 668 |  | 8442 | 652 | -3897 | -3897 | -3897 | Critical Branch | ID schedules | 0 | NA | 29 | 16 | 45 | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 7693 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 1830 |  | 8518 | 651 |  | 8518 | 651 | -1661 | -1661 | -1661 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | 7966 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 1930 |  | 8518 | 651 |  | 8518 | 651 | -1618 | -1618 | -1618 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | -425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 425 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 2030 |  | 8271 | 651 |  | 8266 | 651 | -1493 | -1493 | -1493 | ID schedules | ID schedules | 0 | NA | 5 | 0 | 5 | 0 | 1 | 140 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 147 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 2130 |  | 8414 | 688 |  | 8414 | 688 | -4903 | -4903 | -4903 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 2230 |  | 8414 | 688 |  | 8414 | 688 | -4903 | -4903 | -4903 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-26 | June | 2330 |  | 7853 | 713 |  | 7853 | 713 | -4298 | -4298 | -4298 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-27 | June | 1230 | 8736 |  |  | 8735 |  |  | -3348 | -3348 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 1330 | 8736 |  |  | 8735 |  |  | -3348 | -3348 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 1430 | 8736 |  |  | 8735 |  |  | -3348 | -3348 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 1530 | 8675 |  |  | 8675 |  |  | -2994 | -2994 | -2994 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 1630 | 8663 |  |  | 8663 |  |  | -2989 | -2989 | -2989 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-27 | June | 1730 | 8481 |  |  | 8481 |  |  | -2902 | -2902 | -2902 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | -413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 413 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-27 | June | 1830 |  | 8425 | 673 |  | 8424 | 673 | -3190 | -3190 | -3190 | Critical Branch | ID schedules | 0 | NA | 1 | 0 | 1 | 0 | 1 | -393 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 421 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-27 | June | 1930 |  | 8425 | 673 |  | 8424 | 673 | -3190 | -3190 | -3190 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 2030 |  | 8425 | 673 |  | 8424 | 673 | -3190 | -3190 | -3190 | Critical Branch | Critical Branch | 0 | NA | 1 | 0 | 1 | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 2130 |  | 8695 | 708 |  | 8563 | 708 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | 0 | NA | 132 | 0 | 132 | 0 | 1 | 137 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 2230 |  | 8695 | 708 |  | 8563 | 708 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | 0 | NA | 132 | 0 | 132 | 0 | 1 | 137 | None | Reduction because NTC over thermal limit on border | 425 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-27 | June | 2330 |  | 8135 | 733 |  | 7984 | 733 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 151 | 0 | 151 | 0 | 1 | 157 | None | Reduction because NTC over thermal limit on border | 415 | None | Reduction because NTC over thermal limit on border | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-28 | June | 1230 | 6049 |  |  | 6049 |  |  | -1478 | -1478 | -1478 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1330 | 6111 |  |  | 6111 |  |  | -1420 | -1420 | -1420 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1430 | 5999 |  |  | 5999 |  |  | -1445 | -1445 | -1445 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1530 | 7273 |  |  | 7004 |  |  | -48 | -48 | 132 | Critical Branch | ID schedules | 0 | 269 | NA | NA | NA | 132 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1630 | 8050 |  |  | 8050 |  |  | -821 | -821 | -821 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1730 | 7380 |  |  | 7380 |  |  | -388 | -388 | -388 | ID schedules | ID schedules | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1830 | 8894 |  |  | 8417 |  |  | -3804 | -3804 | -3438 | Critical Branch | ID schedules | 0 | 477 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 1930 | 8894 |  |  | 8470 |  |  | -3776 | -3776 | -3407 | Critical Branch | ID schedules | 0 | 424 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 2030 | 8894 |  |  | 8066 |  |  | -3837 | -3837 | -3295 | Critical Branch | ID schedules | 0 | 828 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 2130 | 8795 |  |  | 7680 |  |  | -1367 | -1367 | -161 | Critical Branch | ID schedules | 0 | 1115 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 2230 | 8795 |  |  | 7668 |  |  | -1367 | -1367 | -114 | Critical Branch | ID schedules | 0 | 1127 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-28 | June | 2330 | 8195 |  |  | 7059 |  |  | -748 | -748 | 517 | Critical Branch | ID schedules | 0 | 1136 | NA | NA | NA | 517 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 1230 | 4033 |  |  | 4033 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 351 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 1330 | 4061 |  |  | 4061 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 348 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 1430 | 4058 |  |  | 4058 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 306 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 1530 |  | 6434 | 688 |  | 4515 | 688 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 0 | NA | 1919 | 0 | 1919 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 386 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-29 | June | 1630 |  | 6857 | 719 |  | 6857 | 719 | 0 | 0 | 0 | ID schedules | ID schedules | 0 | NA | 0 | 0 | 0 | 0 | 1 | 158 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 370 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-29 | June | 1730 |  | 7808 | 688 |  | 7808 | 688 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 0 | NA | 0 | 0 | 0 | 0 | 1 | 159 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 415 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked
2024-06-29 | June | 1830 | 8821 |  |  | 8383 |  |  | -4265 | -4265 | -3828 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 438 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 331 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 1930 | 8821 |  |  | 7875 |  |  | -4265 | -4265 | -3214 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 946 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 393 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 2030 | 8821 |  |  | 7867 |  |  | -4265 | -4265 | -3206 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 954 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 411 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 2130 | 8392 |  |  | 7772 |  |  | -970 | -970 | -233 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 620 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 409 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | 7994 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 2230 | 8392 |  |  | 7755 |  |  | -970 | -970 | -213 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 637 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 409 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-29 | June | 2330 | 8392 |  |  | 7703 |  |  | -970 | -970 | -150 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 689 | NA | NA | NA | 0 | 1 | 160 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 409 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 1230 | 6376 |  |  | 6376 |  |  | -5026 | -5026 | -5026 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 1330 | 6376 |  |  | 6376 |  |  | -5026 | -5026 | -5026 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 1430 | 6376 |  |  | 6376 |  |  | -5026 | -5026 | -5026 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 1530 | 6664 |  |  | 6663 |  |  | 0 | 0 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-30 | June | 1630 | 6664 |  |  | 6663 |  |  | 0 | 0 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-30 | June | 1730 | 6664 |  |  | 6663 |  |  | 0 | 0 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1 | NA | NA | NA | 0 | 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
2024-06-30 | June | 1830 | 7457 |  |  | 7457 |  |  | -2616 | -2616 | -2616 | ID schedules | TTC Validation phase - bilateral reduction | 0 | 0 | NA | NA | NA | 0 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 1930 | 6853 |  |  | 6498 |  |  | -2088 | -2088 | -1715 | Critical Branch | ID schedules | 0 | 355 | NA | NA | NA | 0 | 1 | 27 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 315 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 2030 | 6853 |  |  | 4718 |  |  | -2088 | -2088 | -89 | Critical Branch | ID schedules | 0 | 2135 | NA | NA | NA | 0 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 315 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 2130 | 7303 |  |  | 6187 |  |  | -522 | -522 | 431 | Critical Branch | ID schedules | 0 | 1116 | NA | NA | NA | 431 | 1 | 70 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 338 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 2230 | 7303 |  |  | 4647 |  |  | -515 | -515 | 1696 | Critical Branch | ID schedules | 0 | 2656 | NA | NA | NA | 1696 | 1 | -188 | None | Because of high redispatch the leftover intraday capacity was set to 0 | 336 | None | Because of high redispatch the leftover intraday capacity was set to 0 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None
2024-06-30 | June | 2330 | 6703 |  |  | 4917 |  |  | -4 | -4 | 1487 | Critical Branch | TTC Validation phase - bilateral reduction | 0 | 1786 | NA | NA | NA | 1487 | 1 | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | -10000 | None | ATC blocked | None | None | None

## ID 70% reduction
ID 70% reduction results
|  |  | TTC Adjustment |  |  | ANTC |  | LimitedBy
BD | Month | TS | TTC_Full_Import | TTCImport | TTCExport | ANTCfinal | ANTCfeasible | Adjustment | 70% reduction | % reduction | Category
2025-04-01 | April | 1830 |  | 6460 | 942 | 1026 | 10 | Minimum Margin | 1016 | 99.03% | above 1000 MW
2025-04-01 | April | 2030 |  | 6996 | 1072 | 614 | 10 | Minimum Margin | 604 | 98.37% | [500-1000] MW
2025-04-06 | April | 2130 |  | 6280 | 597 | 4045 | 0 | Critical Branch | 4045 | 100% | above 1000 MW
2025-04-16 | April | 1830 |  | 5727 | 701 | 27977 | 0 | Critical Branch | 27977 | 100% | above 1000 MW
2025-04-16 | April | 1930 |  | 6698 | 701 | 26649 | 0 | Critical Branch | 26649 | 100% | above 1000 MW
2025-04-16 | April | 2030 |  | 4717 | 701 | 28443 | 0 | Critical Branch | 28443 | 100% | above 1000 MW
2025-04-21 | April | 1530 |  | -566 | 2522 | 7645 | 0 | Critical Branch | 7645 | 100% | above 1000 MW
2025-04-21 | April | 1630 |  | 1089 | 2696 | 6244 | 0 | Critical Branch | 6244 | 100% | above 1000 MW
2025-04-21 | April | 1730 |  | 1089 | 2728 | 6270 | 0 | Critical Branch | 6270 | 100% | above 1000 MW
2025-04-29 | April | 2030 |  | 3914 | 473 | 585 | 11 | Minimum Margin | 574 | 98.12% | [500-1000] MW
2025-04-29 | April | 2130 |  | 4840 | 190 | 2094 | 2 | Minimum Margin | 2092 | 99.9% | above 1000 MW
2025-04-29 | April | 2330 |  | 5554 | 194 | 1140 | 2 | Minimum Margin | 1138 | 99.82% | above 1000 MW
2025-05-09 | May | 2030 | 6234 |  |  | 13137 | -63 | Critical Branch | 13200 | 100.5% | above 1000 MW
2025-05-09 | May | 2130 | 6947 |  |  | 1371 | 226 | Minimum Margin | 1145 | 83.52% | above 1000 MW
2025-05-09 | May | 2230 | 6881 |  |  | 1437 | 226 | Minimum Margin | 1211 | 84.27% | above 1000 MW
2025-05-09 | May | 2330 | 6343 |  |  | 1945 | 225 | Minimum Margin | 1720 | 88.43% | above 1000 MW
2025-05-15 | May | 1830 |  | 6001 | 588 | 15910 | 0 | Critical Branch | 15910 | 100% | above 1000 MW
2025-05-15 | May | 1930 |  | 6001 | 261 | 15821 | 0 | Critical Branch | 15821 | 100% | above 1000 MW
2025-05-15 | May | 2030 |  | 6001 | 654 | 15948 | 0 | Critical Branch | 15948 | 100% | above 1000 MW
2025-05-17 | May | 1830 |  | 2726 | 821 | 1515 | 25 | Minimum Margin | 1490 | 98.35% | above 1000 MW
2025-05-19 | May | 1230 |  | 4893 | 413 | 18928 | 0 | Critical Branch | 18928 | 100% | above 1000 MW
2025-05-19 | May | 1330 |  | 5261 | 209 | 18872 | 0 | Critical Branch | 18872 | 100% | above 1000 MW
2025-05-19 | May | 1430 |  | 4539 | 99 | 18934 | 0 | Critical Branch | 18934 | 100% | above 1000 MW
2025-05-22 | May | 1630 | 6274 |  |  | 20051 | -43 | Critical Branch | 20094 | 100.2% | above 1000 MW
2025-05-22 | May | 1730 | 6274 |  |  | 20051 | -43 | Critical Branch | 20094 | 100.2% | above 1000 MW
2025-05-24 | May | 2030 |  | 5331 | 2 | 11809 | -73 | Critical Branch | 11882 | 100.6% | above 1000 MW
2025-05-26 | May | 2130 |  | 4759 | 460 | 1220 | 215 | Minimum Margin | 1005 | 82.38% | above 1000 MW
2025-05-26 | May | 2230 |  | 5745 | 463 | 299 | 215 | Minimum Margin | 84 | 28.09% | below 500 MW
2025-05-26 | May | 2330 |  | 5404 | -214 | 720 | 215 | Minimum Margin | 505 | 70.14% | [500-1000] MW
2025-05-29 | May | 2030 | 5663 |  |  | 3220 | -33 | Critical Branch | 3253 | 101% | above 1000 MW
2025-06-06 | June | 1530 |  | 5329 | 243 | 1028 | 197 | Minimum Margin | 831 | 80.84% | above 1000 MW
2025-06-06 | June | 1630 |  | 5338 | 554 | 1468 | 197 | Minimum Margin | 1271 | 86.58% | above 1000 MW
2025-06-06 | June | 1730 |  | 5330 | 145 | 1285 | 197 | Minimum Margin | 1088 | 84.67% | above 1000 MW
2025-06-07 | June | 1230 | 2316 |  |  | 11437 | -55 | Critical Branch | 11492 | 100.5% | above 1000 MW
2025-06-07 | June | 1330 | 2316 |  |  | 11437 | -55 | Critical Branch | 11492 | 100.5% | above 1000 MW
2025-06-07 | June | 1430 | 2316 |  |  | 11437 | -55 | Critical Branch | 11492 | 100.5% | above 1000 MW
2025-06-16 | June | 2130 |  | 7829 | 605 | 270 | 0 | Critical Branch | 270 | 100% | below 500 MW
2025-06-16 | June | 2230 |  | 7829 | 605 | 270 | 0 | Critical Branch | 270 | 100% | below 500 MW
2025-06-16 | June | 2330 |  | 7269 | 630 | 856 | 0 | Critical Branch | 856 | 100% | [500-1000] MW
2025-06-17 | June | 1530 | 9264 |  |  | 1513 | 364 | Minimum Margin | 1149 | 75.94% | above 1000 MW
2025-06-17 | June | 1630 | 9264 |  |  | 1513 | 364 | Minimum Margin | 1149 | 75.94% | above 1000 MW
2025-06-17 | June | 1730 | 9264 |  |  | 1513 | 364 | Minimum Margin | 1149 | 75.94% | above 1000 MW
2025-06-17 | June | 2030 |  | 8252 | 850 | 584 | 343 | Minimum Margin | 241 | 41.27% | [500-1000] MW
2025-06-18 | June | 2130 |  | 7247 | 599 | 1058 | 246 | Minimum Margin | 812 | 76.75% | above 1000 MW
2025-06-18 | June | 2230 |  | 7760 | 599 | 789 | 246 | Minimum Margin | 543 | 68.82% | [500-1000] MW
2025-06-18 | June | 2330 |  | 7200 | 548 | 1132 | 246 | Minimum Margin | 886 | 78.27% | above 1000 MW
2025-06-21 | June | 2030 |  | 7472 | 667 | 397 | 214 | Minimum Margin | 183 | 46.1% | below 500 MW
2025-06-21 | June | 2130 |  | 7330 | 773 | 1547 | 206 | Minimum Margin | 1341 | 86.68% | above 1000 MW
2025-06-21 | June | 2230 |  | 7330 | 773 | 1547 | 206 | Minimum Margin | 1341 | 86.68% | above 1000 MW
2025-06-21 | June | 2330 |  | 6538 | 804 | 2159 | 206 | Minimum Margin | 1953 | 90.46% | above 1000 MW
2025-06-23 | June | 2130 | 8666 |  |  | 1050 | 216 | Minimum Margin | 834 | 79.43% | above 1000 MW
2025-06-23 | June | 2230 | 8666 |  |  | 1050 | 216 | Minimum Margin | 834 | 79.43% | above 1000 MW
2025-06-23 | June | 2330 | 8065 |  |  | 1639 | 215 | Minimum Margin | 1424 | 86.88% | above 1000 MW

## ID validation reduction
ID Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | NTC-Import | NTC-Export | ANTC |  |  | LimitedBy |  | TTC Validation Reduction |  |  | Reason for TTC Reduction |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction |  |  | Reason for TTC Reduction
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | AT-IT FR-IT | IT-AT IT-FR | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | Smoothing | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason
2025-04-01 | April | 2130 | 9316 |  |  | 9305 |  |  |  |  | -1928 | -1928 | -1916 | Critical Branch | Validation phase | 11 | NA | 0 | [5 empty] | CH | 9055 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago
2025-04-01 | April | 2230 | 9316 |  |  | 9140 |  |  |  |  | -1928 | -1928 | -1752 | Critical Branch | Validation phase | 176 | NA | 0 | [5 empty] | CH | 8890 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago
2025-04-02 | April | 2130 | 9506 |  |  | 9499 |  |  |  |  | -3222 | -3222 | -3214 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border
2025-04-02 | April | 2230 | 9506 |  |  | 9499 |  |  |  |  | -3222 | -3222 | -3216 | Critical Branch | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border
2025-04-02 | April | 2330 | 8696 |  |  | 8688 |  |  |  |  | -2502 | -2502 | -2495 | Critical Branch | TTC Validation phase - bilateral reduction | 8 | NA | 0 |  |  | AT | 170 | Reduction because NTC over thermal limit on border
2025-04-03 | April | 1430 | 8075 |  |  | 8062 |  |  |  |  | -2942 | -2942 | -2931 | Critical Branch | TTC Validation phase - bilateral reduction | 13 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-03 | April | 1530 | 8228 |  |  | 8206 |  |  |  |  | -4670 | -4670 | -4653 | Critical Branch | TTC Validation phase - bilateral reduction | 22 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-03 | April | 1630 | 8228 |  |  | 8030 |  |  |  |  | -4670 | -4670 | -4474 | Critical Branch | Validation phase | 198 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border | CH | 7791 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-04-03 | April | 1730 | 9528 |  |  | 7997 |  |  |  |  | -6026 | -6026 | -4498 | Critical Branch | TTC Validation phase - bilateral reduction | 1531 | NA | 0 | [5 empty] | CH | 8274 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | FR | 3000 | Planned outage of Creys-Saint-Vulbas 2 + Praz-Villarodin |  |  |  | IT | -10000 | ATC blocked
2025-04-03 | April | 2130 | 8480 |  |  | 7584 |  |  |  |  | -2596 | -2596 | -1706 | Critical Branch | TTC Validation phase - bilateral reduction | 896 | NA | 0
2025-04-03 | April | 2230 | 8480 |  |  | 8478 |  |  |  |  | -2596 | -2596 | -2595 | Critical Branch | TTC Validation phase - bilateral reduction | 2 | NA | 0
2025-04-05 | April | 1830 | 9112 |  |  | 6742 |  |  |  |  | 0 | 0 | -643 | Critical Branch | TTC Validation phase - bilateral reduction | 2370 | NA | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-05 | April | 1930 | 9112 |  |  | 7556 |  |  |  |  | 0 | 0 | -1239 | Critical Branch | TTC Validation phase - bilateral reduction | 1556 | NA | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-05 | April | 2030 | 9112 |  |  | 8644 |  |  |  |  | 0 | 0 | -2178 | Critical Branch | TTC Validation phase - bilateral reduction | 468 | NA | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-05 | April | 2130 | 9873 |  |  | 9236 |  |  |  |  | 0 | 0 | -1418 | Critical Branch | TTC Validation phase - bilateral reduction | 637 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-05 | April | 2230 | 9873 |  |  | 9236 |  |  |  |  | 0 | 0 | -1418 | Critical Branch | TTC Validation phase - bilateral reduction | 637 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-05 | April | 2330 | 9063 |  |  | 8571 |  |  |  |  | 0 | 0 | -684 | Critical Branch | TTC Validation phase - bilateral reduction | 492 | NA | 0 |  |  | AT | 170 | Reduction because NTC over thermal limit on border |  |  |  | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-15 | April | 1630 | 6952 |  |  | 6951 |  |  |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 1 | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-15 | April | 2130 | 7314 |  |  | 7309 |  |  |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 5 | NA | 0 | [8 empty] | FR | 2000 | Planned outage of Chaffard-Grande-Ile 2
2025-04-18 | April | 1830 | 8675 |  |  | 8225 |  |  |  |  | -4548 | -4548 | -4163 | Critical Branch | Smoothing ramp | 450 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-04-18 | April | 1930 | 8675 |  |  | 8563 |  |  |  |  | -4548 | -4548 | -4438 | Critical Branch | Smoothing ramp | 112 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 1230 | 4493 |  |  | 4467 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 26 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 1330 | 4493 |  |  | 4467 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 26 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 1430 | 4493 |  |  | 4467 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 26 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 1530 | 5349 |  |  | 5288 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 61 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 1630 | 5349 |  |  | 5288 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 61 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 1730 | 5349 |  |  | 5288 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 61 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-19 | April | 2030 | 5515 |  |  | 5514 |  |  |  |  | -1604 | -1604 | -2232 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-04-20 | April | 1830 | 6044 |  |  | 3423 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 2621 | NA | 0 |  |  | AT | 170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 1930 | 6044 |  |  | 4794 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1250 | NA | 0 |  |  | AT | 170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 2030 | 6044 |  |  | 5626 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 418 | NA | 0 |  |  | AT | 170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-24 | April | 1330 | 1532 |  |  | 1507 |  |  |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 25 | NA | 0 |  |  | AT | 170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-24 | April | 1430 | 1858 |  |  | 1851 |  |  |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | 7 | NA | 0 |  |  | AT | 170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-26 | April | 2230 | 9116 |  |  | 9103 |  |  |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 13 | NA | 0 | Smoothing ramp | Smoothing ramp |  |  |  | CH | 7848 | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 RONDISSONE-TRINO
2025-04-28 | April | 1230 | 7481 |  |  | 7446 |  |  |  |  | -3362 | -3362 | -3330 | Critical Branch | TTC Validation phase - bilateral reduction | 35 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-28 | April | 1330 | 7481 |  |  | 7446 |  |  |  |  | -3362 | -3362 | -3330 | Critical Branch | TTC Validation phase - bilateral reduction | 35 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-28 | April | 1430 | 7481 |  |  | 7446 |  |  |  |  | -3362 | -3362 | -3330 | Critical Branch | TTC Validation phase - bilateral reduction | 35 | NA | 0 |  |  | AT | 155 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1230 | 7383 |  |  | 7338 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 45 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1330 | 7383 |  |  | 7338 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 45 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1430 | 7383 |  |  | 7338 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 45 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1530 | 7060 |  |  | 7056 |  |  |  |  | -1777 | -1777 | -1773 | Critical Branch | TTC Validation phase - bilateral reduction | 4 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1630 | 7060 |  |  | 7056 |  |  |  |  | -1777 | -1777 | -1773 | Critical Branch | TTC Validation phase - bilateral reduction | 4 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1730 | 7060 |  |  | 7056 |  |  |  |  | -1777 | -1777 | -1773 | Critical Branch | Critical Branch | 4 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-30 | April | 1530 | 6293 |  |  | 5965 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 328 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-30 | April | 1630 | 6293 |  |  | 5946 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 347 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-30 | April | 1730 | 7193 |  |  | 7049 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | 144 | NA | 0 |  |  | AT | 155 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-03 | May | 1530 | 963 |  |  | 884 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 79 | NA | 0 |  |  | AT | 137 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-09 | May | 2230 | 6881 |  |  | 6860 |  |  |  |  | 1437 | 226 | 1263 | Minimum Margin | ID schedules | 21 | NA | 52 | [8 empty] | FR | 6545 | N-1 Albertville-Rondissone 1 / [FR-IT] Albertville-Rondissone 2 [OPP] [FR]
2025-05-15 | May | 2130 | 7525 |  |  | 7492 |  |  |  |  | 0 | 0 | -1423 | Critical Branch | TTC Validation phase - bilateral reduction | 33 | NA | 0
2025-05-20 | May | 1930 | 6231 |  |  | 6050 |  |  |  |  | 0 | 0 | -2828 | Critical Branch | TTC Validation phase - bilateral reduction | 181 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-20 | May | 2030 | 6231 |  |  | 5805 |  |  |  |  | 0 | 0 | -2679 | Critical Branch | ID schedules | 426 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-25 | May | 2130 | 7123 |  |  | 6536 |  |  |  |  | -1171 | -1171 | -625 | Critical Branch | TTC Validation phase - bilateral reduction | 587 | NA | 0
2025-05-28 | May | 2030 | 6686 |  |  | 6352 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 334 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-28 | May | 2130 | 6686 |  |  | 6668 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 18 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-29 | May | 2130 | 7059 |  |  | 7007 |  |  |  |  | -3353 | -3353 | -3319 | Critical Branch | TTC Validation phase - bilateral reduction | 52 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-29 | May | 2230 | 7059 |  |  | 7007 |  |  |  |  | -3353 | -3353 | -3319 | Critical Branch | TTC Validation phase - bilateral reduction | 52 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-31 | May | 1530 | 6153 |  |  | 4791 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 1362 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-05-31 | May | 1730 | 6153 |  |  | 5817 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 336 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-06-01 | June | 1830 | 6217 |  |  | 3656 |  |  |  |  | -2643 | -2643 | -34 | Critical Branch | Smoothing ramp | 2561 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-06-01 | June | 1930 | 6217 |  |  | 5235 |  |  |  |  | -2643 | -2643 | -1606 | Critical Branch | Smoothing ramp | 982 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-06-01 | June | 2030 | 6217 |  |  | 5998 |  |  |  |  | -2643 | -2643 | -2402 | Critical Branch | Smoothing ramp | 219 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-06-03 | June | 1230 | 6241 |  |  | 6121 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 120 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-03 | June | 1330 | 6241 |  |  | 6147 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 94 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-03 | June | 1430 | 6241 |  |  | 6213 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 28 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-05 | June | 1730 | 5460 |  |  | 4772 |  |  |  |  | 0 | 0 | 9414 | Critical Branch | TTC Validation phase - bilateral reduction | 688 | NA | 9414 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
2025-06-06 | June | 1230 | 6881 |  |  | 5354 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1527 | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
2025-06-06 | June | 1330 | 6881 |  |  | 5354 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1527 | NA | 0 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
2025-06-07 | June | 1230 | 2316 |  |  | 2006 |  |  |  |  | 11437 | -55 | 11528 | Critical Branch | Smoothing ramp | 310 | NA | 36 | Smoothing ramp | Smoothing ramp | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-07 | June | 1330 | 2316 |  |  | 1982 |  |  |  |  | 11437 | -55 | 11579 | Critical Branch | TTC Validation phase - bilateral reduction | 334 | NA | 87 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-07 | June | 1430 | 2316 |  |  | 2000 |  |  |  |  | 11437 | -55 | 11441 | Critical Branch | TTC Validation phase - bilateral reduction | 316 | NA | -51 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-09 | June | 1330 | 6289 |  |  | 6173 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 116 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-06-09 | June | 1730 | 7231 |  |  | 6421 |  |  |  |  | -2046 | -2046 | -1899 | Critical Branch | Smoothing ramp | 810 | NA | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-06-10 | June | 1230 | 7009 |  |  | 6885 |  |  |  |  | 0 | 0 | -3700 | Critical Branch | Validation phase | 124 | NA | 0 | [5 empty] | CH | 6635 | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE
2025-06-10 | June | 1530 | 7046 |  |  | 7033 |  |  |  |  | 0 | 0 | 13116 | Critical Branch | ID schedules | 13 | NA | 13116 | [5 empty] | CH | 6710 | Reduction due to missing redispatch potential
2025-06-10 | June | 1630 | 7046 |  |  | 6982 |  |  |  |  | 0 | 0 | 13067 | Critical Branch | ID schedules | 64 | NA | 13067 | [5 empty] | CH | 6710 | Reduction due to missing redispatch potential
2025-06-10 | June | 1730 | 7046 |  |  | 6751 |  |  |  |  | 0 | 0 | 13401 | Critical Branch | Smoothing ramp | 295 | NA | 13401 | Smoothing ramp | Smoothing ramp |  |  |  | CH | 6710 | Reduction due to missing redispatch potential
2025-06-10 | June | 2130 | 6904 |  |  | 6751 |  |  |  |  | -4853 | -4853 | -4700 | Critical Branch | Smoothing ramp | 153 | NA | 0 | Smoothing ramp | Smoothing ramp
2025-06-11 | June | 1230 | 7205 |  |  | 7139 |  |  |  |  | -1751 | -1751 | -1675 | Critical Branch | TTC Validation phase - bilateral reduction | 66 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-11 | June | 1330 | 7205 |  |  | 7139 |  |  |  |  | -1751 | -1751 | -1675 | Critical Branch | TTC Validation phase - bilateral reduction | 66 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-11 | June | 1430 | 7205 |  |  | 7139 |  |  |  |  | -1751 | -1751 | -1675 | Critical Branch | TTC Validation phase - bilateral reduction | 66 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-13 | June | 1230 | 8328 |  |  | 6629 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1699 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 6616 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | [6 empty] | IT | -10000 | ATC blocked
2025-06-13 | June | 1330 | 8328 |  |  | 6629 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1699 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 6131 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | [6 empty] | IT | -10000 | ATC blocked
2025-06-13 | June | 1430 | 8328 |  |  | 6629 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1699 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5735 | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 NAUDERS-WESTTIROL 1 | [6 empty] | IT | -10000 | ATC blocked
2025-06-13 | June | 1530 | 8328 |  |  | 8030 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 298 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7209 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | [6 empty] | IT | -10000 | ATC blocked
2025-06-13 | June | 1630 | 8328 |  |  | 8030 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 298 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-13 | June | 1730 | 8328 |  |  | 8315 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 13 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-15 | June | 1830 | 9022 |  |  | 7000 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | ID schedules | 2022 | NA | 0 |  |  | AT | 157 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 8054 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-06-15 | June | 1930 | 9022 |  |  | 7892 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1130 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 8609 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
2025-06-15 | June | 2030 | 9022 |  |  | 8783 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 239 | NA | 0 |  |  | AT | 158 | Reduction because NTC over thermal limit on border | CH | 8550 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
2025-06-15 | June | 2130 | 9022 |  |  | 8937 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 85 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border | CH | 8714 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
2025-06-15 | June | 2230 | 9022 |  |  | 8992 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 30 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border
2025-06-15 | June | 2330 | 9022 |  |  | 8992 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 30 | NA | 0 |  |  | AT | 160 | Reduction because NTC over thermal limit on border
2025-06-17 | June | 1530 | 9264 |  |  | 8900 |  |  |  |  | 1513 | 364 | 1513 | Minimum Margin | TTC Validation phase - bilateral reduction | 364 | NA | 364 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 8323 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | [6 empty] | IT | -10000 | ATC blocked
2025-06-17 | June | 1630 | 9264 |  |  | 8900 |  |  |  |  | 1513 | 364 | 1513 | Minimum Margin | TTC Validation phase - bilateral reduction | 364 | NA | 364 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 8748 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | [6 empty] | IT | -10000 | ATC blocked
2025-06-17 | June | 1730 | 9264 |  |  | 9246 |  |  |  |  | 1513 | 364 | 1163 | Minimum Margin | TTC Validation phase - bilateral reduction | 18 | NA | 14 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-19 | June | 1230 | 7260 |  |  | 7239 |  |  |  |  | -698 | -698 | -676 | Critical Branch | ID schedules | 21 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 1330 | 7260 |  |  | 7239 |  |  |  |  | -698 | -698 | -676 | Critical Branch | ID schedules | 21 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 1430 | 7260 |  |  | 7239 |  |  |  |  | -698 | -698 | -676 | Critical Branch | ID schedules | 21 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 1530 | 8265 |  |  | 7911 |  |  |  |  | -1213 | -1213 | -866 | Critical Branch | ID schedules | 354 | NA | 0 | [5 empty] | CH | 7724 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | [6 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 1630 | 8265 |  |  | 8187 |  |  |  |  | -1213 | -1213 | -1144 | Critical Branch | ID schedules | 78 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 1730 | 8265 |  |  | 8187 |  |  |  |  | -1213 | -1213 | -1144 | Critical Branch | ID schedules | 78 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-06-20 | June | 1530 | 8998 |  |  | 8932 |  |  |  |  | -6409 | -6409 | -6315 | Critical Branch | ID schedules | 66 | NA | 0 |  |  | AT | -364 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-20 | June | 1630 | 8998 |  |  | 8993 |  |  |  |  | -6409 | -6409 | -6400 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-20 | June | 1730 | 8998 |  |  | 8993 |  |  |  |  | -6409 | -6409 | -6400 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-20 | June | 2330 | 8118 |  |  | 8117 |  |  |  |  | -5664 | -5664 | -5663 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2025-06-21 | June | 1230 | 4958 |  |  | 4500 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 458 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 3288 | Missing CNEC in CC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 NAUDERS-WESTTIROL 1 | [6 empty] | IT | -10000 | ATC blocked
2025-06-21 | June | 1330 | 4958 |  |  | 4537 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 421 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-21 | June | 1430 | 4958 |  |  | 4535 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 423 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-23 | June | 2130 | 8666 |  |  | 8654 |  |  |  |  | 1050 | 216 | 841 | Minimum Margin | TTC Validation phase - bilateral reduction | 12 | NA | 7 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-23 | June | 2230 | 8666 |  |  | 8654 |  |  |  |  | 1050 | 216 | 841 | Minimum Margin | TTC Validation phase - bilateral reduction | 12 | NA | 7 |  |  | AT | 140 | Reduction because NTC over thermal limit on border
2025-06-23 | June | 2330 | 8065 |  |  | 8053 |  |  |  |  | 1639 | 215 | 1431 | Minimum Margin | TTC Validation phase - bilateral reduction | 12 | NA | 7 |  |  | AT | 160 | Reduction because NTC over thermal limit on border
2024-06-24 | June | 1230 | 6847 |  |  | 6846 |  |  |  |  | 0 | 0 | -3286 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-24 | June | 1330 | 6847 |  |  | 6846 |  |  |  |  | 0 | 0 | -3286 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-24 | June | 1430 | 6847 |  |  | 6846 |  |  |  |  | 0 | 0 | -3286 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-24 | June | 1530 | 6287 |  |  | 6286 |  |  |  |  | 0 | 0 | -4210 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-24 | June | 1630 | 7287 |  |  | 7286 |  |  |  |  | 0 | 0 | -5218 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-24 | June | 1730 | 7287 |  |  | 7286 |  |  |  |  | 0 | 0 | -5218 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 |  |  | AT | -274 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-25 | June | 1230 | 7629 |  |  | 7613 |  |  |  |  | -4286 | -4286 | -4254 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-25 | June | 1330 | 7629 |  |  | 7613 |  |  |  |  | -4286 | -4286 | -4254 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-25 | June | 1430 | 7629 |  |  | 7613 |  |  |  |  | -4286 | -4286 | -4254 | Critical Branch | TTC Validation phase - bilateral reduction | 16 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-25 | June | 1530 | 8238 |  |  | 8181 |  |  |  |  | -2128 | -2128 | -2096 | Critical Branch | TTC Validation phase - bilateral reduction | 57 | NA | 0 |  |  | AT | 140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-25 | June | 1630 | 8238 |  |  | 8237 |  |  |  |  | -2128 | -2128 | -2127 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-25 | June | 1730 | 8838 |  |  | 8837 |  |  |  |  | -2719 | -2719 | -2718 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-27 | June | 1230 | 8736 |  |  | 8735 |  |  |  |  | -3348 | -3348 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-27 | June | 1330 | 8736 |  |  | 8735 |  |  |  |  | -3348 | -3348 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-27 | June | 1430 | 8736 |  |  | 8735 |  |  |  |  | -3348 | -3348 | -3345 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-28 | June | 1530 | 7273 |  |  | 7004 |  |  |  |  | -48 | -48 | 132 | Critical Branch | ID schedules | 269 | NA | 132 | [14 empty] | IT | -10000 | ATC blocked
2024-06-28 | June | 1830 | 8894 |  |  | 8417 |  |  |  |  | -3804 | -3804 | -3438 | Critical Branch | ID schedules | 477 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2024-06-28 | June | 1930 | 8894 |  |  | 8470 |  |  |  |  | -3776 | -3776 | -3407 | Critical Branch | ID schedules | 424 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2024-06-28 | June | 2030 | 8894 |  |  | 8066 |  |  |  |  | -3837 | -3837 | -3295 | Critical Branch | ID schedules | 828 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2024-06-28 | June | 2130 | 8795 |  |  | 7680 |  |  |  |  | -1367 | -1367 | -161 | Critical Branch | ID schedules | 1115 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2024-06-28 | June | 2230 | 8795 |  |  | 7668 |  |  |  |  | -1367 | -1367 | -114 | Critical Branch | ID schedules | 1127 | NA | 0 | [14 empty] | IT | -10000 | ATC blocked
2024-06-28 | June | 2330 | 8195 |  |  | 7059 |  |  |  |  | -748 | -748 | 517 | Critical Branch | ID schedules | 1136 | NA | 517 | [14 empty] | IT | -10000 | ATC blocked
2024-06-29 | June | 1830 | 8821 |  |  | 8383 |  |  |  |  | -4265 | -4265 | -3828 | Critical Branch | TTC Validation phase - bilateral reduction | 438 | NA | 0 | Smoothing ramp | Smoothing ramp | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-29 | June | 1930 | 8821 |  |  | 7875 |  |  |  |  | -4265 | -4265 | -3214 | Critical Branch | TTC Validation phase - bilateral reduction | 946 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-29 | June | 2030 | 8821 |  |  | 7867 |  |  |  |  | -4265 | -4265 | -3206 | Critical Branch | TTC Validation phase - bilateral reduction | 954 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-29 | June | 2130 | 8392 |  |  | 7772 |  |  |  |  | -970 | -970 | -233 | Critical Branch | TTC Validation phase - bilateral reduction | 620 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7994 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | [6 empty] | IT | -10000 | ATC blocked
2024-06-29 | June | 2230 | 8392 |  |  | 7755 |  |  |  |  | -970 | -970 | -213 | Critical Branch | TTC Validation phase - bilateral reduction | 637 | NA | 0 | Smoothing ramp | Smoothing ramp | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-29 | June | 2330 | 8392 |  |  | 7703 |  |  |  |  | -970 | -970 | -150 | Critical Branch | TTC Validation phase - bilateral reduction | 689 | NA | 0 |  |  | AT | 160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-30 | June | 1530 | 6664 |  |  | 6663 |  |  |  |  | 0 | 0 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-30 | June | 1630 | 6664 |  |  | 6663 |  |  |  |  | 0 | 0 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-30 | June | 1730 | 6664 |  |  | 6663 |  |  |  |  | 0 | 0 | -1733 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0
2024-06-30 | June | 1930 | 6853 |  |  | 6498 |  |  |  |  | -2088 | -2088 | -1715 | Critical Branch | ID schedules | 355 | NA | 0 |  |  | AT | 27 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-30 | June | 2030 | 6853 |  |  | 4718 |  |  |  |  | -2088 | -2088 | -89 | Critical Branch | ID schedules | 2135 | NA | 0 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-30 | June | 2130 | 7303 |  |  | 6187 |  |  |  |  | -522 | -522 | 431 | Critical Branch | ID schedules | 1116 | NA | 431 |  |  | AT | 70 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-30 | June | 2230 | 7303 |  |  | 4647 |  |  |  |  | -515 | -515 | 1696 | Critical Branch | ID schedules | 2656 | NA | 1696 |  |  | AT | -188 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2024-06-30 | June | 2330 | 6703 |  |  | 4917 |  |  |  |  | -4 | -4 | 1487 | Critical Branch | TTC Validation phase - bilateral reduction | 1786 | NA | 1487 | [14 empty] | IT | -10000 | ATC blocked
2025-04-05 | April | 1230 |  | 2595 | 1234 |  | 2189 | 1137 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 503 | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
2025-04-05 | April | 1330 |  | 2595 | 1234 |  | 1410 | 1140 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1279 | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
2025-04-05 | April | 1430 |  | 2595 | 1234 |  | 496 | 1202 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2131 | 0 | [8 empty] | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
2025-04-05 | April | 1630 |  | 3986 | 701 |  | 3949 | 701 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 37 | 0
2025-04-07 | April | 1930 |  | 5844 | 935 |  | 5011 | 935 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 833 | 0 | [5 empty] | CH | 4289 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE
2025-04-07 | April | 2030 |  | 5488 | 877 |  | 4671 | 909 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 785 | 0 | [5 empty] | CH | 4078 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2
2025-04-08 | April | 1330 |  | 6570 | 72 |  | 6552 | 72 |  |  | 15247 | -72 | 15247 | ID schedules | ID schedules | NA | 18 | -72 | [5 empty] | CH | 6379 | Reduction due to missing redispatch potential | [6 empty] | IT | -10000 | ATC blocked
2025-04-08 | April | 1930 |  | 5684 | 684 |  | 5186 | 677 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 505 | 0 | [5 empty] | CH | 4645 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | FR | 3200 | Planned outage of Creys-Saint-Vulbas 2 |  |  |  | IT | -10000 | ATC blocked
2025-04-10 | April | 1830 |  | 7263 | 875 |  | 7263 | 558 |  |  | 12410 | -81 | 12410 | ID schedules | Smoothing ramp | NA | 317 | -81 | [8 empty] | FR | 2600 | Planned outage of Creys-Saint-Vulbas 2
2025-04-11 | April | 1830 |  | 7547 | 489 |  | 7547 | 484 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 5 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-04-11 | April | 2230 |  | 7387 | 699 |  | 7387 | 698 |  |  | -2560 | -2560 | -2560 | ID schedules | ID schedules | NA | 1 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-04-11 | April | 2330 |  | 6874 | 684 |  | 6874 | 677 |  |  | -2093 | -2093 | -2093 | ID schedules | ID schedules | NA | 7 | 0
2025-04-12 | April | 1530 |  | 7430 | 815 |  | 4456 | 815 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 2974 | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-04-12 | April | 1630 |  | 6540 | 877 |  | 6447 | 877 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 93 | 0 |  |  | AT | 43 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-12 | April | 1730 |  | 7430 | 815 |  | 6463 | 139 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1643 | 0
2025-04-12 | April | 2130 |  | 7791 | 699 |  | 7791 | 689 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 10 | 0
2025-04-12 | April | 2230 |  | 7791 | 549 |  | 7791 | 534 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 15 | 0
2025-04-13 | April | 1530 |  | 6980 | 889 |  | 6474 | 800 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 595 | 0
2025-04-13 | April | 1630 |  | 7280 | 889 |  | 7039 | 732 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 398 | 0
2025-04-13 | April | 1730 |  | 7280 | 889 |  | 7029 | 380 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 760 | 0
2025-04-14 | April | 1930 |  | 4237 | 881 |  | 3855 | 881 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 382 | 0 | [5 empty] | CH | 3435 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | [6 empty] | IT | -10000 | ATC blocked
2025-04-16 | April | 1930 |  | 6698 | 701 |  | 6177 | 701 |  |  | 26649 | 0 | 26649 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 521 | 0 | [8 empty] | FR | 2200 | N-1 CHAFFARD-G.ILE
2025-04-20 | April | 1230 |  | 3778 | 3113 |  | 584 | 2429 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3878 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 1330 |  | 3778 | 3113 |  | 584 | 1553 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 4754 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 1430 |  | 3778 | 3113 |  | 584 | 677 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 5630 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 1530 |  | 3278 | 2874 |  | 508 | 479 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 5165 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 1630 |  | 3278 | 2874 |  | 482 | 460 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 5210 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 1730 |  | 3278 | 2874 |  | -320 | -1312 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 7784 | 0 |  |  | AT | -170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-20 | April | 2130 |  | 5262 | 907 |  | 5260 | 907 |  |  | -1266 | -1266 | -1266 | ID schedules | TTC Validation phase - bilateral reduction | NA | 2 | 0 |  |  | AT | -170 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-21 | April | 1230 |  | 3278 | 2874 |  | 1443 | 2612 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2097 | 0 |  |  | AT | 435 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-21 | April | 1330 |  | 3278 | 2874 |  | 1442 | 2608 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2102 | 0 |  |  | AT | 435 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-21 | April | 1430 |  | 3278 | 2874 |  | 1443 | 2609 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2100 | 0 |  |  | AT | 435 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-21 | April | 1530 |  | -566 | 2522 |  | -566 | 2441 |  |  | 7645 | 0 | 7645 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 81 | 0 |  |  | AT | 435 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-04-21 | April | 1830 |  | 6376 | 1217 |  | 2907 | 1217 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3469 | 0 |  |  | AT | -170 | Reduction because NTC over thermal limit on border
2025-04-21 | April | 1930 |  | 6376 | 1217 |  | 4443 | 907 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2243 | 0
2025-04-21 | April | 2030 |  | 6376 | 1217 |  | 5559 | 907 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1127 | 0
2025-04-22 | April | 2230 |  | 3969 | 703 |  | 3961 | 703 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 8 | 0
2025-04-26 | April | 1430 |  | 1728 | 450 |  | 1317 | 418 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 443 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-04-26 | April | 1530 |  | 2003 | 618 |  | 1500 | 585 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 536 | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-04-26 | April | 1730 |  | 2003 | 618 |  | 1579 | 618 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 424 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-04-28 | April | 2330 |  | 6074 | 925 |  | 6074 | 323 |  |  | -2585 | -2585 | -2585 | ID schedules | TTC Validation phase - bilateral reduction | NA | 602 | 0 |  |  | AT | 417 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 1930 |  | 6643 | 462 |  | 6198 | 249 |  |  | -1172 | -1172 | -1172 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 658 | 0 |  |  | AT | 109 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-04-29 | April | 2230 |  | 8503 | 176 |  | 6800 | 176 |  |  | -2082 | -2082 | -2082 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1703 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-04-30 | April | 2230 |  | 7745 | 873 |  | 6964 | 873 |  |  | -4348 | -4348 | -4348 | ID schedules | Smoothing ramp | NA | 781 | 0 | Smoothing ramp | Smoothing ramp
2025-05-01 | May | 1230 |  | 1136 | 915 |  | 956 | 862 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 233 | 0 |  |  | AT | 305 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 1330 |  | 1136 | 915 |  | 956 | 862 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 233 | 0 |  |  | AT | 305 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 1430 |  | 1136 | 915 |  | -45 | 904 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1192 | 0 |  |  | AT | 305 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 1530 |  | 1925 | 645 |  | 819 | 645 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1106 | 0 |  |  | AT | 49 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 1630 |  | 1158 | 678 |  | 1146 | 678 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 12 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 1830 |  | 7263 | 864 |  | 3924 | 711 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 3492 | 0 |  |  | AT | -114 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 1930 |  | 7263 | 864 |  | 4833 | 639 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2655 | 0 |  |  | AT | -115 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-01 | May | 2030 |  | 7263 | 864 |  | 5633 | 644 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1850 | 0 |  |  | AT | -116 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-02 | May | 1930 |  | 7047 | 614 |  | 6774 | 614 |  |  | -2899 | -2899 | -2899 | ID schedules | Smoothing ramp | NA | 273 | 0 | Smoothing ramp | Smoothing ramp
2025-05-02 | May | 2230 |  | 7602 | 766 |  | 7390 | 766 |  |  | -2772 | -2772 | -2772 | ID schedules | ID schedules | NA | 212 | 0 | [5 empty] | CH | 6279 | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 145%
2025-05-02 | May | 2330 |  | 7420 | 670 |  | 7365 | 710 |  |  | -2332 | -2332 | -2332 | ID schedules | ID schedules | NA | 15 | 0
2025-05-03 | May | 1230 |  | 638 | 614 |  | 637 | 614 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0 |  |  | AT | 47 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-03 | May | 1330 |  | 870 | 516 |  | 362 | 275 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 749 | 0 | Smoothing ramp | Smoothing ramp | AT | 44 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-03 | May | 2030 |  | 6650 | 466 |  | 6650 | 424 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 42 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-03 | May | 2330 |  | 6908 | 130 |  | 6908 | 128 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 2 | 0
2025-05-04 | May | 1330 |  | 886 | 97 |  | 870 | 97 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | NA | 16 | 0 |  |  | AT | 48 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-04 | May | 1430 |  | 946 | 97 |  | 883 | 97 |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | NA | 63 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-04 | May | 1930 |  | 6552 | 899 |  | 5787 | 899 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | NA | 765 | 0 | Smoothing ramp | Smoothing ramp
2025-05-04 | May | 2030 |  | 7173 | 865 |  | 6612 | 452 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 974 | 0
2025-05-06 | May | 1730 |  | 5427 | 646 |  | 5428 | 560 |  |  | -858 | -858 | -858 | ID schedules | ID schedules | NA | 85 | 0
2025-05-06 | May | 2330 |  | 5869 | 191 |  | 5862 | 191 |  |  | -633 | -633 | -633 | ID schedules | ID schedules | NA | 7 | 0
2025-05-07 | May | 2230 |  | 7536 | 625 |  | 7520 | 625 |  |  | -2579 | -2579 | -2579 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 16 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
2025-05-08 | May | 1330 |  | 5522 | 250 |  | 5522 | 247 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 3 | 0
2025-05-10 | May | 1230 |  | 2675 | 828 |  | 1229 | 828 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1446 | 0
2025-05-10 | May | 1330 |  | 2675 | 828 |  | 1374 | 784 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1345 | 0
2025-05-10 | May | 1430 |  | 2675 | 828 |  | 1361 | 791 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1351 | 0
2025-05-10 | May | 1530 |  | 2064 | 620 |  | 1894 | 567 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 223 | 0 |  |  | AT | 402 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-10 | May | 1930 |  | 5932 | 586 |  | 5892 | 586 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 40 | 0
2025-05-10 | May | 2030 |  | 6393 | 598 |  | 6379 | 598 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 14 | 0
2025-05-11 | May | 1230 |  | 2767 | 1116 |  | 1398 | 1044 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1441 | 0 |  |  | AT | 340 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-11 | May | 1330 |  | 2767 | 1116 |  | 1399 | 1044 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 1440 | 0 |  |  | AT | 339 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-11 | May | 1430 |  | 2767 | 1116 |  | 1399 | 1044 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1440 | 0 |  |  | AT | 340 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-11 | May | 1530 |  | 1957 | 480 |  | 1345 | 462 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 630 | 0 |  |  | AT | 357 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-12 | May | 1230 |  | 7056 | 775 |  | 6622 | 579 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 630 | 0
2025-05-12 | May | 1330 |  | 7056 | 775 |  | 6622 | 535 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 674 | 0
2025-05-12 | May | 1430 |  | 7056 | 775 |  | 6622 | 447 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 762 | 0
2025-05-13 | May | 2330 |  | 5667 | 477 |  | 5667 | 466 |  |  | -2497 | -2497 | -2497 | ID schedules | TTC Validation phase - bilateral reduction | NA | 11 | 0
2025-05-14 | May | 1330 |  | 7599 | 114 |  | 7554 | 116 |  |  | -1272 | -1272 | -1272 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 43 | 0 |  |  | AT | 377 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7335 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | [6 empty] | IT | -10000 | ATC blocked
2025-05-16 | May | 1230 |  | 6795 | 693 |  | 6026 | 654 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 808 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-16 | May | 1330 |  | 6795 | 693 |  | 6006 | 654 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 828 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-16 | May | 1430 |  | 6795 | 693 |  | 6006 | 654 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 828 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-17 | May | 1330 |  | 2030 | 455 |  | 1666 | 440 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 379 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-17 | May | 1430 |  | 2030 | 455 |  | 1648 | 417 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 420 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-17 | May | 1830 |  | 2726 | 821 |  | 2702 | 821 |  |  | 1515 | 25 | 1515 | Minimum Margin | Smoothing ramp | NA | 24 | 25 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-05-18 | May | 1230 |  | 930 | 677 |  | 643 | 677 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 287 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-18 | May | 1430 |  | 1104 | 677 |  | 1103 | 677 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 1 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-18 | May | 1930 |  | 4638 | 865 |  | 4245 | 865 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | NA | 393 | 0 | Smoothing ramp | Smoothing ramp | [12 empty] | IT | -10000 | ATC blocked
2025-05-19 | May | 1330 |  | 5261 | 209 |  | 5146 | 209 |  |  | 18872 | 0 | 18872 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 115 | 0 |  |  | AT | 107 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-19 | May | 1830 |  | 5517 | 772 |  | 5517 | 750 |  |  | -4434 | -4434 | -4434 | ID schedules | TTC Validation phase - bilateral reduction | NA | 22 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-05-22 | May | 2230 |  | 7530 | 654 |  | 7519 | 654 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 11 | 0
2025-05-24 | May | 1930 |  | 5705 | 652 |  | 4997 | 652 |  |  | 11675 | -73 | 11675 | ID schedules | TTC Validation phase - bilateral reduction | NA | 708 | -73 |  |  | AT | 20 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 5454 | Reduction due to missing redispatch potential | [6 empty] | IT | -10000 | ATC blocked
2025-05-25 | May | 1630 |  | 1237 | 865 |  | 1234 | 865 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 3 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-05-25 | May | 1930 |  | 4488 | 753 |  | 4133 | 753 |  |  | -1124 | -1124 | -1124 | ID schedules | Smoothing ramp | NA | 355 | 0 | Smoothing ramp | Smoothing ramp
2025-05-26 | May | 1830 |  | 5543 | 535 |  | 5543 | 533 |  |  | -3137 | -3137 | -3137 | ID schedules | ID schedules | NA | 2 | 0
2025-05-26 | May | 2230 |  | 5745 | 463 |  | 5626 | 444 |  |  | 299 | 215 | 299 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 138 | 215 | [8 empty] | FR | 2816 | Process fail during TSO validation phase
2025-05-26 | May | 2330 |  | 5404 | -214 |  | 5285 | -214 |  |  | 720 | 215 | 720 | Minimum Margin | ID schedules | NA | 119 | 215 | [8 empty] | FR | 2606 | Process fail during TSO validation phase
2025-05-27 | May | 1930 |  | 7164 | 505 |  | 7164 | 466 |  |  | -4459 | -4459 | -4459 | ID schedules | ID schedules | NA | 39 | 0
2025-06-02 | June | 1230 |  | 235 | 2864 |  | -67 | 3155 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 11 | 0 |  |  | AT | -96 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-02 | June | 1330 |  | 235 | 2864 |  | 29 | 2864 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 206 | 0 |  |  | AT | 0 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-02 | June | 1430 |  | 235 | 2864 |  | -131 | 3155 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 75 | 0 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-02 | June | 1930 |  | 5386 | 827 |  | 5098 | 827 |  |  | 3263 | -16 | 3263 | ID schedules | TTC Validation phase - bilateral reduction | NA | 288 | -16 |  |  | AT | -160 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-04 | June | 2330 |  | 5299 | 186 |  | 5299 | 180 |  |  | -2528 | -2528 | -2528 | ID schedules | TTC Validation phase - bilateral reduction | NA | 6 | 0
2025-06-05 | June | 1830 |  | 5922 | 526 |  | 5922 | 462 |  |  | -2351 | -2351 | -2351 | ID schedules | ID schedules | NA | 64 | 0
2025-06-05 | June | 2130 |  | 6501 | 653 |  | 6501 | 631 |  |  | -3099 | -3099 | -3099 | ID schedules | ID schedules | NA | 22 | 0
2025-06-06 | June | 1530 |  | 5329 | 243 |  | 5132 | 243 |  |  | 1028 | 197 | 1028 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 197 | 197 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
2025-06-06 | June | 1630 |  | 5338 | 554 |  | 5133 | 537 |  |  | 1468 | 197 | 1468 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 222 | 197 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
2025-06-06 | June | 1730 |  | 5330 | 145 |  | 5133 | 128 |  |  | 1285 | 197 | 1285 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 214 | 197 | [8 empty] | FR | 1700 | Planned outage of Chaffard-Grande-Ile 2
2025-06-06 | June | 1830 |  | 7150 | 233 |  | 6575 | 233 |  |  | -4906 | -4906 | -4906 | Critical Branch | Smoothing ramp | NA | 575 | 0 | Smoothing ramp | Smoothing ramp
2025-06-07 | June | 1830 |  | 7397 | 654 |  | 7086 | 654 |  |  | -1022 | -1022 | -1022 | ID schedules | TTC Validation phase - bilateral reduction | NA | 311 | 0
2025-06-07 | June | 2130 |  | 7927 | 654 |  | 7913 | 654 |  |  | -1303 | -1303 | -1303 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 14 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
2025-06-07 | June | 2230 |  | 7927 | 617 |  | 7913 | 621 |  |  | -1303 | -1303 | -1303 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 10 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
2025-06-07 | June | 2330 |  | 7587 | 75 |  | 7534 | 75 |  |  | -950 | -950 | -950 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 53 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
2025-06-08 | June | 2130 |  | 8046 | 669 |  | 7910 | 669 |  |  | -1781 | -1781 | -1781 | ID schedules | TTC Validation phase - bilateral reduction | NA | 136 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
2025-06-08 | June | 2230 |  | 8189 | 517 |  | 8153 | 517 |  |  | -1803 | -1803 | -1803 | ID schedules | TTC Validation phase - bilateral reduction | NA | 36 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
2025-06-09 | June | 1930 |  | 5659 | 106 |  | 5659 | 99 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 7 | 0
2025-06-09 | June | 2230 |  | 5659 | 101 |  | 5659 | 91 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 10 | 0
2025-06-10 | June | 1830 |  | 4775 | 272 |  | 4775 | 271 |  |  | 3878 | 0 | 3878 | ID schedules | ID schedules | NA | 1 | 0
2025-06-11 | June | 2130 |  | 7234 | 783 |  | 7138 | 783 |  |  | -1480 | -1480 | -1480 | ID schedules | TTC Validation phase - bilateral reduction | NA | 96 | 0 |  |  | AT | -135 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-12 | June | 1830 |  | 6866 | 718 |  | 6836 | 718 |  |  | -1593 | -1593 | -1593 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 30 | 0 |  |  | AT | 401 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-12 | June | 1930 |  | 6866 | 718 |  | 6830 | 718 |  |  | -1593 | -1593 | -1593 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 36 | 0 |  |  | AT | 395 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-12 | June | 2030 |  | 6866 | 718 |  | 6295 | 718 |  |  | -1593 | -1593 | -1593 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 571 | 0 |  |  | AT | -140 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-12 | June | 2130 |  | 7540 | 654 |  | 7236 | 654 |  |  | -2829 | -2829 | -2829 | ID schedules | ID schedules | NA | 304 | 0 |  |  | AT | -20 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-12 | June | 2330 |  | 7322 | 611 |  | 7322 | 606 |  |  | -2702 | -2702 | -2702 | ID schedules | ID schedules | NA | 5 | 0 |  |  | AT | 415 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7008 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | [6 empty] | IT | -10000 | ATC blocked
2025-06-13 | June | 2030 |  | 7969 | 643 |  | 7968 | 643 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-06-14 | June | 1230 |  | 3809 | 173 |  | 3330 | 173 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 479 | 0 |  |  | AT | 345 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-14 | June | 1330 |  | 3809 | 173 |  | 3566 | 173 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 243 | 0 |  |  | AT | 345 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-14 | June | 1430 |  | 3927 | 374 |  | 3813 | 374 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 114 | 0 |  |  | AT | 345 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-14 | June | 1530 |  | 6391 | 620 |  | 3991 | 620 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 2400 | 0 |  |  | AT | 417 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-14 | June | 1630 |  | 5918 | 651 |  | 5364 | 651 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 554 | 0 |  |  | AT | 421 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-15 | June | 1230 |  | 4203 | 1979 |  | 1566 | 1979 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 2637 | 0 |  |  | AT | 394 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-15 | June | 1330 |  | 4203 | 1979 |  | 1566 | 1979 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 2637 | 0 |  |  | AT | 394 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-15 | June | 1430 |  | 4203 | 1979 |  | 1062 | 1979 |  |  | 0 | 0 | 0 | GSK Limitation | ID schedules | NA | 3141 | 0 |  |  | AT | 193 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-16 | June | 2030 |  | 7071 | 585 |  | 7070 | 585 |  |  | 6599 | 0 | 6599 | ID schedules | TTC Validation phase - bilateral reduction | NA | 1 | 0
2025-06-17 | June | 1930 |  | 8325 | 845 |  | 8035 | 816 |  |  | 290 | 290 | 290 | Adjustment reached | TTC Validation phase - bilateral reduction | NA | 319 | 290 |  |  | AT | 173 | Reduction because NTC over thermal limit on border | CH | 7555 | Reduction due to missing redispatch potential
2025-06-17 | June | 2030 |  | 8252 | 850 |  | 7906 | 844 |  |  | 584 | 343 | 584 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 352 | 343 |  |  | AT | -47 | Reduction because NTC over thermal limit on border
2025-06-17 | June | 2230 |  | 7655 | 816 |  | 7609 | 816 |  |  | -1357 | -1357 | -1357 | ID schedules | TTC Validation phase - bilateral reduction | NA | 46 | 0 | [5 empty] | CH | 7390 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-06-18 | June | 2130 |  | 7247 | 599 |  | 7096 | 599 |  |  | 1058 | 246 | 1058 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 151 | 246
2025-06-18 | June | 2230 |  | 7760 | 599 |  | 7515 | 599 |  |  | 789 | 246 | 789 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 245 | 246
2025-06-18 | June | 2330 |  | 7200 | 548 |  | 7198 | 548 |  |  | 1132 | 246 | 1132 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 2 | 246
2025-06-19 | June | 1830 |  | 8727 | 755 |  | 8635 | 755 |  |  | -6049 | -6049 | -6049 | Critical Branch | ID schedules | NA | 92 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 1930 |  | 8847 | 755 |  | 8836 | 755 |  |  | -6113 | -6113 | -6113 | Critical Branch | ID schedules | NA | 11 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 2030 |  | 8801 | 755 |  | 8306 | 755 |  |  | -6110 | -6110 | -6110 | Critical Branch | ID schedules | NA | 495 | 0 | [14 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 2130 |  | 8575 | 693 |  | 8555 | 693 |  |  | -337 | -337 | -337 | Critical Branch | ID schedules | NA | 20 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 2230 |  | 8575 | 693 |  | 8555 | 693 |  |  | -337 | -337 | -337 | Critical Branch | ID schedules | NA | 20 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-06-19 | June | 2330 |  | 8249 | 735 |  | 8178 | 735 |  |  | 214 | 214 | 214 | Adjustment reached | ID schedules | NA | 71 | 214 |  |  | AT | 415 | Reduction because NTC over thermal limit on border | [9 empty] | IT | -10000 | ATC blocked
2025-06-21 | June | 1530 |  | 7113 | 654 |  | 5042 | 654 |  |  | -825 | -825 | -825 | Critical Branch | ID schedules | NA | 2071 | 0 |  |  | AT | 318 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-21 | June | 1630 |  | 7181 | 654 |  | 6922 | 654 |  |  | -792 | -792 | -792 | Critical Branch | ID schedules | NA | 259 | 0 |  |  | AT | 380 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-21 | June | 1730 |  | 6997 | 654 |  | 6740 | 654 |  |  | -639 | -639 | -639 | Critical Branch | ID schedules | NA | 257 | 0 |  |  | AT | 380 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-21 | June | 2030 |  | 7472 | 667 |  | 7397 | 667 |  |  | 397 | 214 | 397 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 75 | 214
2025-06-21 | June | 2330 |  | 6538 | 804 |  | 6332 | 668 |  |  | 2159 | 206 | 2159 | Minimum Margin | ID schedules | NA | 342 | 206 | [5 empty] | CH | 4986 | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL
2025-06-22 | June | 1230 |  | 2607 | 292 |  | 2330 | 380 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 189 | 0
2025-06-22 | June | 1430 |  | 2607 | 292 |  | 2000 | 292 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 607 | 0
2025-06-22 | June | 1530 |  | 4786 | 882 |  | 3126 | 879 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1663 | 0 |  |  | AT | 409 | Reduction because NTC over thermal limit on border
2025-06-22 | June | 1630 |  | 4392 | 974 |  | 4393 | 957 |  |  | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 16 | 0 |  |  | AT | -91 | Reduction because NTC over thermal limit on border
2025-06-22 | June | 1730 |  | 5816 | 974 |  | 5816 | 952 |  |  | 0 | 0 | 0 | ID schedules | ID schedules | NA | 22 | 0 |  |  | AT | -142 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
2025-06-22 | June | 1830 |  | 7209 | 781 |  | 7180 | 781 |  |  | -218 | -218 | -218 | ID schedules | TTC Validation phase - bilateral reduction | NA | 29 | 0 |  |  | AT | 415 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
45467 | June | 2330 |  | 7017 | 744 |  | 6978 | 744 |  |  | -672 | -672 | -672 | Critical Branch | Min import NTC Threshold | NA | 39 | 0
45468 | June | 1830 |  | 8688 | 718 |  | 8271 | 718 |  |  | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 417 | 0
45468 | June | 1930 |  | 8688 | 718 |  | 8271 | 718 |  |  | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 417 | 0
45468 | June | 2030 |  | 8688 | 718 |  | 8271 | 718 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 417 | 0
45468 | June | 2130 |  | 7767 | 951 |  | 7767 | 926 |  |  | -1553 | -1553 | -1553 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 25 | 0 |  |  | AT | 192 | Reduction because NTC over thermal limit on border
45468 | June | 2230 |  | 7767 | 951 |  | 7767 | 926 |  |  | -1553 | -1553 | -1553 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 25 | 0 |  |  | AT | 192 | Reduction because NTC over thermal limit on border
45468 | June | 2330 |  | 7050 | 996 |  | 6944 | 969 |  |  | -958 | -958 | -958 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 133 | 0 |  |  | AT | 369 | Reduction because NTC over thermal limit on border
45469 | June | 1630 |  | 7071 | 668 |  | 7043 | 668 |  |  | -2141 | -2141 | -2141 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 28 | 0 |  |  | AT | 425 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
45469 | June | 1730 |  | 8471 | 668 |  | 8442 | 652 |  |  | -3897 | -3897 | -3897 | Critical Branch | ID schedules | NA | 45 | 0 |  |  | AT | 425 | Because of high redispatch the leftover intraday capacity was set to 0 | CH | 7693 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | [6 empty] | IT | -10000 | ATC blocked
45469 | June | 2030 |  | 8271 | 651 |  | 8266 | 651 |  |  | -1493 | -1493 | -1493 | ID schedules | ID schedules | NA | 5 | 0 |  |  | AT | 147 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
45470 | June | 1830 |  | 8425 | 673 |  | 8424 | 673 |  |  | -3190 | -3190 | -3190 | Critical Branch | ID schedules | NA | 1 | 0 |  |  | AT | 421 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked
45470 | June | 1930 |  | 8425 | 673 |  | 8424 | 673 |  |  | -3190 | -3190 | -3190 | Critical Branch | Critical Branch | NA | 1 | 0
45470 | June | 2030 |  | 8425 | 673 |  | 8424 | 673 |  |  | -3190 | -3190 | -3190 | Critical Branch | Critical Branch | NA | 1 | 0
45470 | June | 2130 |  | 8695 | 708 |  | 8563 | 708 |  |  | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 132 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
45470 | June | 2230 |  | 8695 | 708 |  | 8563 | 708 |  |  | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 132 | 0 |  |  | AT | 425 | Reduction because NTC over thermal limit on border
45470 | June | 2330 |  | 8135 | 733 |  | 7984 | 733 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 151 | 0 |  |  | AT | 415 | Reduction because NTC over thermal limit on border
45472 | June | 1530 |  | 6434 | 688 |  | 4515 | 688 |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 1919 | 0 |  |  | AT | 386 | Because of high redispatch the leftover intraday capacity was set to 0 | [9 empty] | IT | -10000 | ATC blocked

## ID FLAGS processing
TSO | Long description | Type | # of TS
AT | Reduction because NTC over thermal limit on border | NTC over thermal limit | 50
AT | Because of high redispatch the leftover intraday capacity was set to 0 | Redispatch | 122
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 7
CH | Missing CNEC in CC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: N-1 RONDISSONE-TRINO | Missing CNEC in CC | 1
CH | Expected overloading on the following CNEC: CNE: 220kV Avise - Riddes [OPP] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 1
CH | Reduction due to missing redispatch potential | Redispatch | 6
CH | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza [DIR], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 2
CH | Expected overloading on the following CNEC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 NAUDERS-WESTTIROL 1 | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 3
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 2
CH | Missing CNEC in CC: CNE: 380kV Pradella-Nauders 2 [OPP] [CH], C: N-1 NAUDERS-WESTTIROL 1 | Missing CNEC in CC | 1
CH | N-1: 380 kV Rondissone-Trino 2 (352) Constraint 220 kV Airolo-Y/All'Acqua 145% | Outage | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza [DIR] [CH], C: N-2 Gorlago-Piancamuno + Robbia-Gorlago | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-1 BOIS TOLLOT-ROMANEL | Overload | 2
CH | Expected overloading on the following CNEC: CNE: 220kV Pressy-Vallorcine [OPP] [CH], C: N-2 ALBERTVILLE-GRANDE ILE | Overload | 4
FR | Planned outage of Creys-Saint-Vulbas 2 + Praz-Villarodin | Outage | 1
FR | Planned outage of Creys-Saint-Vulbas 2 | Outage | 12
FR | Planned outage of Chaffard-Grande-Ile 2 | Outage | 8
FR | N-1 Albertville-Rondissone 1 / [FR-IT] Albertville-Rondissone 2 [OPP] [FR] | Overload | 1
FR | N-1 CHAFFARD-G.ILE | Overload | 1
FR | Process fail during TSO validation phase | Process Fail | 2
IT | ATC blocked | ATC Blocked | 188
Smoothing ramp | Smoothing ramp | Smoothing | 25